## GSP
Grid Supply Point Name | Break Fault level vs Rating (kA) | Latitude | Longitude | Transformer Nameplate rating (MVA) | Sum of Quoted Generation (MVA) | Minimum Load (MW) | Maximum Load (MW) | Contracted Generation (MVA) | Available Headroom Capacity (MVA) | Reverse Powerflow Capability (%) | Upstream Status | Transmission Works | Transmission Reinforcement Completion Date | Downstream Status | Distribution Works | Distribution Reinforcement Completion Date | SoW Needed? | Part of SWAN? | Other Constraints | Voltage (kV) | Site Classification
AMERSHAM | 10.19/15.3 | 51.664252 | -0.655125 | Shared Site | 0.00 | 27.60 | 99.40 | 48.60 | 266.60 | 95 | Unconstrained |  |  | Unconstrained |  |  | Not known | No | None Known | 400/132 | Green
AXMINSTER | 11.24/21.9 | 50.786889 | -2.921556 | Shared Site | 0.00 | 24.50 | 120.00 | 197.52 | 5.5 (additional through SOW or headroom transfer) | 95 | Constrained | NATIONAL GRID CONSTRAINED Hotwiring of the Hinkley Point – Melksham 1 and 2 circuits to increase their thermal rating (NGET-RI-33539 Re-conductor the Fleet - Lovedean OHL circuits to increase capacity (NGET-RI-31671-2) Re-conductor the Bramley - Fleet OHL circuits to increase capacity (NGET-RI-31671-1) Creation of a new South West Operational Tripping Scheme (OTS) at Taunton (NGET-RI-30752) | 31st October 2024 (Interim constraints prior to completion) | Partially Constrained | 132kV circuit reinforcement includes 0.3km circuit1 cable section as part of a Dual 132kV Cable | 01/03/22 | No | Yes | Due to reverse power back to 132kV network the 29km ,132kV Axminstaer-Yeovil OHL reached to the minimum summer rating rate. | 400/132 | Red
BOTLEY WOOD GSP | 11.07/40.0 | 50.884797 | -1.232586 | 315.00 | 0.00 | 45.30 | 169.00 | 128.21 | 13.9 (additional through SOW or headroom transfer) | 95 | Constrained | NATIONAL GRID CONSTRAINED Re-conductor the Fleet - Lovedean OHL circuits to increase capacity (NGET-RI-31671-2) Re-conductor the Bramley - Fleet OHL circuits to increase capacity (NGET-RI-31671-1) Creation of a new South West Operational Tripping Scheme (OTS) at Taunton (NGET-RI-30752) | 31st October 2024 (Interim constraints prior to completion) | Unconstrained |  |  | No | Yes | Proximity to triggering SoW | 400/132 | Amber
BRAMLEY (ANDO-THAT) | 10.15/NA* | 51.337490 | -1.076474 | 274.00 | 0.00 | 73.60 | 223.20 | 230.00 | 80.00 | 95 | Unconstrained |  |  | Partially Constrained | Andover to be fed by Melksham, swapping Amesbury-Andover supplies. Ashford Hill compound - Thatcham 132kV reconfiguration scheme. | 01/06/21 | Yes | Yes | Moderate proximity to thermal rating for Bramley- Amesbury 132kV circt under FCO. No 132kV substation at Bramley just transformer feeder circuits (*). | 400/132 | Green
BRAMLEY (BASI) | 11.61/NA* | 51.337491 | -1.076475 | 255.00 | 52.60 | 67.00 | 202.00 | 252.00 | 55.00 | 95 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | No 132kV substation at Bramley just transformer feeder circuits(*). | 400/132 | Green
CHICKERELL GSP | 14.96/15.3 | 50.623078 | -2.488705 | 290.00 | 0.00 | 24.30 | 93.70 | 105.88 | 22.6 (additional through SOW or headroom transfer) | 95 | Constrained | NATIONAL GRID CONSTRAINED Hotwiring of the Hinkley Point – Melksham 1 and 2 circuits to increase their thermal rating (NGET-RI-33539) Re-conductor the Fleet - Lovedean OHL circuits to increase capacity (NGET-RI-31671-2) Re-conductor the Bramley - Fleet OHL circuits to increase capacity (NGET-RI-31671-1) Creation of a new South West Operational Tripping Scheme (OTS) at Taunton (NGET-RI-30752) | 31st October 2024 (Interim constraints prior to completion) | Unconstrained |  |  | No | Yes | There is no 132kV network at Chickerell GSP, Will requier a third BSP transformer due to reverse power issue. Limited available physical space. | 400/132 | Red
COWLEY | 14.20/31.5 | 51.723597 | -1.189040 | 864.00 | 0.00 | 221.50 | 725.00 | 868.54 | 0.9 (additional through SOW or headroom transfer) | 95 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Moderate proximity to thermal rating on 132kV circt Cowley- Witney/Yarnton under FCO | 400/132 | Green
EALING | 19.82/21.9 | 51.501834 | -0.295982 | 360.00 | 0.00 | 104.30 | 280.40 | 11.11 | 318.00 | 95 | Unconstrained |  |  | Unconstrained |  |  | Not known | No | Moderate proximity to fault rating. | 275/66 | Green
EAST CLAYDON | 10.52/TBC* | 51.926714 | -0.909202 | Shared site | 0.00 | 120.00 | 535.30 | 216.46 | SOW to be submitted due to limited fault level headroom. | 95 | Partially Constrained |  |  | Partially Constrained |  |  | Yes | No | Pending energization - new site. | 400/132 | Amber
FAWLEY | 19.54/31.5 | 50.820726 | -1.330683 | 480.00 | 0.00 | 134.60 | 344.70 | 823.00 | 0.00 | 95 | Constrained | NATIONAL GRID CONSTRAINED Re-conductor the Fleet - Lovedean OHL circuits to increase capacity. (NGET-RI-31671-2) Re-conductor the Bramley - Fleet OHL circuits to increase capacity. (NGET-RI-31671-1) Creation of a new South West Operational Tripping Scheme (OTS) at Taunton. (NGET-RI-30752) | 31st October 2024 (Interim constraints prior to completion) | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 400/132 | Red
FLEET BRAMLEY | 25.03/31.5 | 51.249996 | -0.881384 | 2016.00 | 52.60 | 578.00 | 1379.00 | 629.00 | GSP under SOW. Headroom TBC following response from NG | 95 | Constrained | NATIONAL GRID CONSTRAINED Re-conductor the Bramley - Fleet OHL circuits to increase capacity (NGET-RI-31671-1) Creation of a new South West Operational Tripping Scheme (OTS) at Taunton. (NGET-RI-30752) | 31st October 2024 (Interim constraints prior to completion) | Partially Constrained |  |  | Yes | Yes | Proximity to thermal rating on short section of MAID-WOKI 132kV circts. No 132kV S/S at Bramley just transformer feeder circuits. Moderate proximity to thermal rating for WOKHAM-BRACK-CAMB under SCO. | 400/132 | Amber
IVER 132KV | 19.15/20.0 | 51.541153 | -0.497034 | 936.00 | 99.00 | 356.00 | 632.70 | 286.00 | 480.00 | 95 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | Close to thermal limit on Iver - Upton/Chalvey Spring/Summer | 400/132 | Green
IVER 66KV | 15.57/40.0 | 51.541153 | -0.497034 | 299.00 | 0.00 | 83.50 | 240.10 | 0.00 | 234.00 | 95 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | Moderate proximity to thermal rating for 66kV circuit Iver to Northolt under FCO | 275/66 | Green
LALEHAM | 17.88/31.5 | 51.424606 | -0.469260 | Shared site | 0.00 | 139.30 | 357.30 | 176.70 | 270.00 | 95 | Unconstrained |  |  | Unconstrained |  |  | Not known | No | Moderate Proximity to capacity rating for Laleham to Staines 132kV circt under FCO | 275/132 | Green
LOVEDEAN | 14.70/25.0 | 50.917078 | -1.040164 | 876.00 | 0.00 | 222.00 | 651.37 | 545.84 | 21.48 (additional through SOW or headroom transfer) | 95 | Constrained | NATIONAL GRID CONSTRAINED Re-conductor the Fleet - Lovedean OHL circuits to increase capacity. (NGET-RI-31671-2) Re-conductor the Bramley - Fleet OHL circuits to increase capacity. (NGET-RI-31671-1) Creation of a new South West Operational Tripping Scheme (OTS) at Taunton. (NGET-RI-30752) | 31st October 2024 (Interim constraints prior to completion) | Partially Constrained |  |  | No | Yes | Moderate proximity to L-E fault level issue. | 400/132 | Amber
MANNINGTON GSP | 257/25 | 50.846472 | -1.894512 | 960.00 | 20.00 | 231.00 | 835.05 | 750.00 | 41.3 (additional through SOW or headroom transfer) | 95 | Constrained | NATIONAL GRID CONSTRAINED Hotwiring of the Hinkley Point – Melksham 1 and 2 circuits to increase their thermal rating (NGET-RI-33539) Re-conductor the Fleet - Lovedean OHL circuits to increase capacity. (NGET-RI-31671-2) Re-conductor the Bramley - Fleet OHL circuits to increase capacity. (NGET-RI-31671-1) Creation of a new South West Operational Tripping Scheme (OTS) at Taunton. (NGET-RI-30752) | 31st October 2024 (Interim constraints prior to completion) | Partially Constrained | Replacement of A205 CB, reinforcement of section of Mannington- Salisbury 132kV circt | 01/06/21 | Yes | Yes | Any new connection will trigger Mannington GSP 132kV CBs reinforcement | 400/132 | Amber
MELKSHAM | 201/31.5 | 51.391871 | -2.150384 | Shared site | 0.00 | 126.40 | 642.70 | 994.09 | SoW for SGT thermal constraint | 95 | Partially Constrained |  |  | Partially Constrained | Andover to be fed by Melksham, swapping Amesbury-Andover supplies. | 01/09/22 | Yes | Yes | No spare bay at Melksham GSP for 132kV connections. Proximity to L-E fault level issue. N-2 SGT capacity contraint | 400/132 | Amber
MINETY | 15.14/40.0 | 51.607484 | -2.001223 | 885.00 | 157.60 | 107.90 | 725.50 | 958.80 | ANMS for SGT N-2 capacity | 95 | Constrained | National Grid reinforcement works required for saturated N-1 SGT capacity, estimated connection date for new applications is 2025-2026 |  | Partially Constrained |  |  | Yes | Yes | No spare bay at Minety GSP for 132kV connections. Future connections on Minety GSP will need ANM under N-2, due to NG SGT constraints. N-1 SGT capacity issue. | 400/132 | Red
NORTH HYDE | 14.29/25.0 | 51.499295 | -0.411410 | 300.00 | 0.00 | 110.00 | 290.10 | 0.00 | 370.00 | 95 | Unconstrained |  |  | Unconstrained |  |  | Not known | No | None Known | 275/66 | Green
NURSLING | 19.06/25.0 | 50.940897 | -1.487940 | 576.00 | 50.00 | 122.90 | 424.00 | 326.03 | 147.50 | 95 | Constrained | NATIONAL GRID CONSTRAINED Re-conductor the Fleet - Lovedean OHL circuits to increase capacity. (NGET-RI-31671-2) Re-conductor the Bramley - Fleet OHL circuits to increase capacity. (NGET-RI-31671-1) Creation of a new South West Operational Tripping Scheme (OTS) at Taunton. (NGET-RI-30752) | 31st October 2024 (Interim constraints prior to completion) | Partially Constrained |  |  | No | Yes | Proximity to L-E fault level issue. Constraints might be needed for when Fawley-Nursling GSPs are solidly coupled. | 400/132 | Amber
WILLESDEN | 16.27/21.9 | 51.534938 | -0.257056 | Shared Site | 0.00 | 117.90 | 228.10 | 5.97 | 434.00 | 95 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 275/66 | Green
Test

## BSP
Bulk Supply Point Name | Corresponding GSP | Break Fault level vs Rating (kA) | Latitude | Longitude | TransformerNameplate Rating (MVA) | Sum of Quoted Generation (MVA) | Minimum Load (MW) | Maximum Load (MW) | Contracted Generation (MVA) | Available Headroom Capacity (MVA) | Reverse Powerflow Capability (%) | Upstream Status | Transmission Works | Transmission Reinforcement Completion Date | Downstream Status | Distribution Works | Distribution Reinforcement Completion Date | SoW Needed? | Part of SWAN? | Other Constraints | Voltage (kV) | Site Classification
LOUDWATER | AMERSHAM | 14.71/18.4 | 51.612574 | -0.692875 | 90.00 | 0.00 | 27.70 | 99.40 | 48.60 | 56.27 |  | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 132/33 | Green
YEOVIL | AXMINSTER | 17.05/25.0 | 50.949910 | -2.605143 | 90.00 | 0.00 | 24.50 | 120.00 | 97.52 | 4.00 |  | Constrained |  |  | Constrained | Update DOC setting for RPF, AVC upgrade | 01/03/2021 | Yes | Yes | Proximity to thermal rating on short section of 132kV circt Axminster-Yeovil under FCO, 29km of 132kV Axminster-Yeovil OHL has reached the thermal rating | 132/33 | Red
BOTLEY WOOD | BOTLEY WOOD GSP | 14.86/25.0 | 50.884798 | -1.232586 | 90.00 | 0.00 | 11.40 | 46.99 | 83.90 | 16.00 |  | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 132/33 | Green
NETLEY COMMON | BOTLEY WOOD GSP | 12.25/25 | 50.905556 | -1.324945 | 90.00 | 0.00 | 32.95 | 112.15 | 41.80 | 65.00 |  | Unconstrained |  |  | Partially Constrained | AVC & load blinder reinforcement,C switchgear reinforcement (FL Results include new rating) | 01/03/2021 | No | Yes | Proximity to make fault rating | 132/33 | Amber
AMESBURY | BRAMLEY (ANDO-THAT) | 10.04/25.0 | 51.183529 | -1.774710 | 90.00 | 0.00 | 17.10 | 56.87 | 27.74 | 0.00 |  | Constrained |  |  | Constrained | Andover-Amesbury reconfiguration scheme. | 01/06/2021 | Yes | No | limited by Ashfordhill-Andover 132kV circuit, totally full | 132/33 | Red
THATCHAM | BRAMLEY (ANDO-THAT) | 19.06/25 | 51.394510 | -1.242144 | 195.00 | 0.00 | 44.71 | 166.45 | 64.23 | 130.00 |  | Unconstrained |  |  | Partially Constrained |  |  | Yes | No | No spare bay AND/OR space for extension | 132/33 | Amber
BASINGSTOKE T1A & T2A | BRAMLEY (BASI) | 13.49/17.5 | 51.269820 | -1.067740 | 78.00 | 52.63 | 13.40 | 43.18 | 37.95 | 33.00 |  | Unconstrained |  |  | Partially Constrained |  |  | Yes | No | No spare bay AND/OR space for extension | 132/32 | Amber
BASINGSTOKE T1B & T2B | BRAMLEY (BASI) | 13.90/17.5 | 51.269820 | -1.067740 | 90.00 | 25.00 | 16.40 | 68.58 | 56.41 | 55.00 |  | Unconstrained |  |  | Partially Constrained |  |  | Yes | No | No spare bay AND/OR space for extension | 132/33 | Amber
BASINGSTOKE T3 & T4 | BRAMLEY (BASI) | 10.87/17.5 | 51.269820 | -1.067740 | 90.00 | 0.00 | 12.50 | 40.06 | 54.00 | 55.00 |  | Unconstrained |  |  | Partially Constrained |  |  | Yes | No | No spare bay AND/OR space for extension | 132/33 | Amber
CHICKERELL | CHICKERELL GSP | 16.5/25 | 50.623078 | -2.488705 | 90.00 | 9.00 | 24.30 | 93.60 | 123.00 | 0.00 |  | Unconstrained |  |  | Unconstrained | AVC and Load blinder reinforcement. Switchgear-C reinforcement (FL results include new rating). Will requier a third BSP transformer | 01/03/2022 | No | Yes | Close proximity to rating on short circt section. | 132/33 | Red
COWLEY LOCAL MAIN | COWLEY | 13.18/25 | 51.710237 | -1.190480 | 90.00 | 0.00 | 13.60 | 75.08 | 14.76 | 28.40 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 132/33 | Green
COWLEY LOCAL RESERVE | COWLEY | 13.14/25.0 | 51.710237 | -1.190480 | 90.00 | 0.00 | 3.20 | 29.53 | 71.69 | 71.60 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 132/33 | Green
DRAYTON | COWLEY | 23.23/25 | 51.631227 | -1.326918 | 228.00 | 18.95 | 23.80 | 132.19 | 131.09 | 20.00 |  | Constrained |  |  | Constrained | AVC and load blinder reinforcements. 2x 132kV cct reinforcements between Cowley - Drayton. 33kV CB reinforcements | 01/05/2023 | Yes | No | Upstream thermal restrictions under FCO. | 132/33 | Red
HEADINGTON | COWLEY | 16.21/17.5 | 51.769350 | -1.212249 | 90.00 | 0.00 | 25.70 | 49.46 | 136.55 | 11.00 |  | Unconstrained |  |  | Constrained | Reconfiguration of Headington-Bicester North BSP groups. |  | Yes | No | Proximity to fault rating. | 132/33 | Red
HIGH WYCOMBE | COWLEY | 12.13/25.0 | 51.622165 | -0.776817 | 90.00 | 0.00 | 28.60 | 97.00 | 18.00 | 21.00 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 132/33 | Green
OXFORD | COWLEY | 13.48/25.0 | 51.750314 | -1.276332 | 102.00 | 0.00 | 27.45 | 89.68 | 0.00 | 8.00 |  | Constrained |  |  | Unconstrained |  |  | Yes | No | Upstream thermal restrictions under FCO. | 132/33 | Amber
WITNEY & YARNTON | COWLEY | 14.15/31.5 | 51.772067 | -1.485304 | 90.00 | 23.95 | 18.29 | 83.59 | 123.36 | 2.00 |  | Constrained |  |  | Unconstrained | load blinder and AVC reinforcements at Yarnton . 132kV circuits between Yarnton - Headington. | 01/05/2023 | Yes | No | None known | 132/33 | Red
BOSTON MANOR | EALING | 14.99/25.0 | 51.489789 | -0.315632 | 38.00 | 0.00 | 10.20 | 32.73 | 8.50 | 38.30 |  | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/11 | Green
BRIDGE ROAD | EALING | 6.85/18.4 | 51.469005 | -0.348937 | 76.00 | 0.00 | 9.70 | 49.71 | 0.00 | 76.60 |  | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/11 | Green
COPLEY DENE | EALING | 21.21/25 | 51.513917 | -0.308862 | 38.00 | 0.00 | 8.70 | 34.81 | 0.00 | 37.30 |  | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/11 | Green
EALING (D) | EALING | 15.83/25.0 | 51.501834 | -0.295982 | 75.00 | 0.00 | 19.10 | 54.70 | 1.60 | 90.00 |  | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/22 | Green
EALING (E) | EALING | 16/25.0 | 51.501834 | -0.295982 | 46.00 | 0.00 | 13.90 | 43.70 | 0.00 | 40.00 |  | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/11 | Green
IRONBRIDGE | EALING | 12.43/25 | 51.508933 | -0.355463 | 38.00 | 0.00 | 8.47 | 33.86 | 1.01 | 40.00 |  | Unconstrained |  |  | Constrained |  |  | No | No | Proximity to fault rating | 66/11 | Red
SOUTHFIELD ROAD | EALING | 15.81/31.5 | 51.503804 | -0.264771 | 40.00 | 0.00 | 5.79 | 39.20 | 0.00 | 40.00 |  | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/11 | Green
BICESTER NORTH | EAST CLAYDON | 12.55/25 | 51.926714 | -1.133272 | 90.00 | 39.11 | 11.10 | 51.00 | 111.22 | 6.80 |  | Constrained |  |  | Unconstrained | Connections pending site energization. | 01/03/2020 | Yes | No | Constrained due to 132kV thermal limitations under FCO.Close proximity to rating on Bicester-Bicester North 33kV circt. | 132/33 | Red
COWES & WOOTTON COMMON | FAWLEY | 20.34/25.0 | 50.710673 | -1.254977 | 182.00 | 0.00 | 28.80 | 126.38 | 118.67 | 0.00 |  | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 132/33 | Red
FAWLEY NORTH | FAWLEY | 15.32/25.0 | 50.838487 | -1.374582 | 133.00 | 0.00 | 69.40 | 98.90 | 0.00 | 0.00 |  | Partially Constrained |  |  | Constrained |  |  | No | Yes | This is constrained due to GSP wide distribution constraints (SSEN-NG). | 132/11 | Red
FAWLEY SOUTH | FAWLEY | 5.32/17.5 | 50.836727 | -1.356769 | 38.50 | 0.00 | 13.80 | 25.96 | 0.00 | 0.00 |  | Partially Constrained |  |  | Constrained |  |  | No | Yes | This is constrained due to GSP wide distribution constraints (SSEN-NG). | 132/11 | Red
LANGLEY | FAWLEY | 16.1/25.0 | 50.810181 | -1.360029 | 58.00 | 0.00 | 5.58 | 25.25 | 19.50 | 0.00 |  | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 132/33 | Red
LYNES COMMON | FAWLEY | 13.61/17.5 | 50.846686 | -1.379131 | 30.00 | 0.00 | 1.21 | 1.98 | 0.00 | 0.00 |  | Constrained |  |  | Constrained |  |  | No | Yes | This is constrained due to GSP wide distribution constraints (SSEN-NG). | 132/11 | Red
ALDERSHOT | FLEET BRAMLEY | 17.18/25 | 51.231748 | -0.770724 | 228.00 | 0.00 | 28.70 | 134.38 | 4.32 | 113.60 |  | Unconstrained |  |  | Unconstrained | Switchgear-C reinforcement (FL results include new rating). | 01/03/2020 | Yes | Yes | None known | 132/33 | Green
ALTON & FERNHURST | FLEET BRAMLEY | 18.04/17.5 | 51.152492 | -0.962212 | 200.00 | 45.97 | 42.70 | 154.96 | 107.00 | 25.00 |  | Unconstrained |  |  | Constrained | Load blinder reinforcement. Switchgear-C reinforcement @ Fernhurst. | 01/06/2021 | Yes | Yes | Proximity to fault rating @Alton. No spare bay and space for extension @Alton. Alton Fernhurst group to be split.Alton BSP group only has 5 MVA generation headroom following split. Fernhurst BSP group | 132/33 | Red
BRACKNELL MAIN | FLEET BRAMLEY | 13.67/25.0 | 51.417271 | -0.764432 | 90.00 | 0.00 | 25.20 | 65.49 | 40.00 | 85.00 |  | Unconstrained |  |  | Partially Constrained |  |  | Yes | Yes | Moderate upstream thermal restrictions for SCO. Moderate proximity to fault level when Bracknell is run solid. | 132/33 | Amber
BRACKNELL RESERVE | FLEET BRAMLEY | 13.81/25.0 | 51.417271 | -0.764432 | 90.00 | 0.00 | 16.10 | 79.36 | 51.21 | 75.00 |  | Unconstrained |  |  | Partially Constrained |  |  | Yes | Yes | Moderate upstream thermal restrictions for SCO. Moderate proximity to fault level when Bracknell is run solid. | 132/33 | Amber
BURGHFIELD MAIN | FLEET BRAMLEY | 16.7/25.0 | 51.429331 | -1.002458 | 90.00 | 0.00 | 18.40 | 85.31 | 35.70 | 38.00 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Moderate proximity to thermal rating on Reading to Burghfield 132kV circt under combined NG & SSE fault events. | 132/33 | Green
BURGHFIELD RESERVE | FLEET BRAMLEY | 14.4/25.0 | 51.429331 | -1.002458 | 90.00 | 0.00 | 15.80 | 65.94 | 18.58 | 75.00 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Moderate proximity to thermal rating on Reading to Burghfield 132kV circt under combined NG & SSE fault events. | 132/33 | Green
CAMBERLEY MAIN | FLEET BRAMLEY | 13.18/25.0 | 51.417271 | -0.764432 | 90.00 |  | 21.60 | 85.25 | 0.00 | 85.00 |  | Unconstrained |  |  | Unconstrained | Switchgear-C reinforcement (FL results include new rating). | 01/03/2020 | Yes | Yes | Moderate upstream thermal restrictions for SCO | 132/33 | Green
CAMBERLEY RESERVE | FLEET BRAMLEY | 12.14/25.0 | 51.327882 | -0.759458 | 90.00 | 0.00 | 17.40 | 74.14 | 1.40 | 100.00 |  | Unconstrained |  |  | Unconstrained | Switchgear-C reinforcement (FL results include new rating). | 01/03/2020 | Yes | Yes | Moderate upstream thermal restrictions for SCO | 132/33 | Green
COXMOOR WOOD | FLEET BRAMLEY | 19.37/25.0 | 51.250827 | -0.879759 | 90.00 | 0.00 | 18.90 | 94.93 | 82.76 | 40.00 |  | Unconstrained |  |  | Partially Constrained | Split of Coxmoor Wood-Pyestock BSP groups. | 01/03/2021 | Yes | Yes | None known | 132/33 | Amber
MAIDENHEAD | FLEET BRAMLEY | 16.63/17.5 | 51.511249 | -0.753591 | 90.00 | 0.00 | 18.14 | 76.90 | 0.22 | 17.40 |  | Partially Constrained |  |  | Constrained |  |  | Yes | Yes | Proximity to fault rating. Proximity to thermal rating on short cable section of Maidenhead- Wokingham/Reading 132kV circt under FCO. | 132/33 | Red
PYESTOCK | FLEET BRAMLEY | 19.81/25.0 | 51.284036 | -0.811515 | 90.00 | 0.00 | 13.78 | 76.28 | 0.00 | 103.00 |  | Unconstrained |  |  | Partially Constrained | Split of Coxmoor Wood-Pyestock BSP groups. | 01/03/2021 | Yes | Yes | None known | 132/33 | Amber
READING | FLEET BRAMLEY | 12.22/17.5 | 51.458778 | -0.926984 | 228.00 | 0.00 | 52.13 | 164.35 | 27.48 | 190.00 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 132/33 | Green
READING TOWN | FLEET BRAMLEY | 13.25/17.5 | 51.461567 | -0.971268 | 9.00 | 0.00 | 16.46 | 68.92 | 0.65 | 100.00 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 132/33 | Green
WOKINGHAM | FLEET BRAMLEY | 12.31/25.0 | 51.402423 | -0.857213 | 90.00 | 0.00 | 6.75 | 45.99 | 0.00 | 65.00 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 132/33 | Green
CHALVEY | IVER 132KV | 22.32/25 | 51.504459 | -0.607243 | 90.00 | 6.00 | 30.10 | 83.70 | 62.24 | 49.50 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 132/33 | Green
CIPPENHAM | IVER 132KV | 14.6/25.0 | 51.507456 | -0.614313 | 90.00 | 0.00 | 9.00 | 66.51 | 10.00 | 89.00 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 132/33 | Green
DENHAM | IVER 132KV | 20.81/25 | 51.578236 | -0.532512 | 90.00 | 20.00 | 18.50 | 75.86 | 50.90 | 40.00 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 132/22 | Green
LONGFORD | IVER 132KV | 16.58/25 | 51.480170 | -0.504886 | 90.00 | 0.00 | 23.00 | 64.36 | 65.70 | 45.70 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | No | Future connections would trigger AVC reinforcement | 132/33 | Green
SLOUGH | IVER 132KV | 24.23/31.15 | 51.526586 | -0.623765 | 270.00 | 0.00 | 23.70 | 95.51 | 118.00 | 106.00 |  | Unconstrained |  |  | Unconstrained | Fault Level Reinforcement triggered. |  | Yes | No | None known | 132/33 | Green
SLOUGH SOUTH | IVER 132KV | 11.93/17.5 | 51.523370 | -0.625592 | 270.00 | 0.00 | 83.70 | 126.90 | 0.00 | 142.60 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 132/33 | Green
UPTON | IVER 132KV | 14.58/25 | 51.504952 | -0.548498 | 76.00 | 0.00 | 12.30 | 37.31 | 9.20 | 83.40 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 132/22 | Green
EAST BEDFONT A | LALEHAM | 14.34/25.0 | 51.453085 | -0.441322 | 76.00 | 0.00 | 25.20 | 72.03 | 6.00 | 79.20 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 132/22 | Green
EAST BEDFONT B | LALEHAM | 11.56/17.5 | 51.453085 | -0.441322 | 26.00 | 0.00 | 7.00 | 25.00 | 0.00 | 24.80 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 132/11 | Green
STAINES | LALEHAM | 15.49/17.5 | 51.438567 | -0.496706 | 300.00 | 0.00 | 95.50 | 222.00 | 170.70 | 54.00 |  | Partially Constrained |  |  | Unconstrained |  |  | Yes | No | Upstream restrictions on Laleham to Staines 132kV circt under FCO | 132/33 | Amber
CHICHESTER & HUNSTON | LOVEDEAN | 17.06/25 | 50.858302 | -0.689564 | 270.00 | 11.00 | 38.90 | 183.50 | 208.00 | 3.00 |  | Unconstrained |  |  | Constrained | AVC &Load blinder and Switchgear-C reinforcement (FL results include new rating).The 75 MVA has already advised to reinforce to 90 MVA (2023).. It will requier a new BSP transformer | 01/03/2022 | No | Yes | BSP transformers limitations under FCO. make fault rating reinforcement. | 132/33 | Red
FAREHAM MAIN | LOVEDEAN | 15.43/25 | 50.833777 | -1.199626 | 90.00 | 0.00 | 17.50 | 83.80 | 104.00 | 14.00 |  | Unconstrained |  |  | Partially Constrained | Fareham-C switchgear upgrade (FL results include new rating) | 01/03/2022 | No | Yes | None known | 132/33 | Amber
FAREHAM RESERVE | LOVEDEAN | 13.10/25 | 50.833777 | -1.199626 | 60.00 | 0.00 | 11.70 | 75.70 | 48.00 | 10.00 |  | Unconstrained |  |  | Partially Constrained | Fareham-C switchgear upgrade (FL results include new rating) | 01/03/2022 | No | Yes | None known | 132/33 | Amber
HAVANT | LOVEDEAN | 18.10/25 | 50.846691 | -0.998200 | 90.00 | 0.00 | 21.50 | 99.90 | 70.00 | 36.00 |  | Unconstrained |  |  | Partially Constrained | Havant AVC reinforcement, Havant-C switchgear reainforcement (FL results include new rating). | 01/07/2022 | No | Yes | None known | 132/33 | Green
PORTSMOUTH | LOVEDEAN | 16.1/25.0 | 50.793272 | -1.101781 | 90.00 | 0.00 | 21.00 | 106.00 | 21.00 | 89.00 |  | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 132/33 | Green
WYMERING & FORT WIDLEY | LOVEDEAN | 13.82/25.0 | 50.845201 | -1.078129 | 60.00 | 0.00 | 34.00 | 116.00 | 87.35 | 88.00 |  | Unconstrained |  |  | Unconstrained | Wymering AVC reinforcement | 01/03/2021 | No | Yes | None known | 132/33 | Green
ARNEWOOD | MANNINGTON GSP | 13.5/13.1 | 50.774654 | -1.631282 | 60.00 | 0.00 | 13.60 | 51.58 | 16.35 | 50.30 |  | Constrained |  |  | Constrained | ARNEWOOD BSP 33kV CB reinforcement | 01/12/2023 | Yes | Yes | Any new connection will trigger Mannington GSP 132kV CBs reinforcemen | 132/33 | Red
BOURNEMOUTH | MANNINGTON GSP | 19.44/25.0 | 50.731517 | -1.912581 | 150.00 | 0.00 | 39.90 | 142.36 | 14.55 | 152.00 |  | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Any new connection will trigger Mannington GSP 132kV CBs reinforcemen | 132/33 | Amber
CHRISTCHURCH | MANNINGTON GSP | 19.1/25 | 50.737610 | -1.779546 | 90.00 | 0.00 | 13.30 | 56.40 | 26.80 | 0.00 |  | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Any new connection will trigger Mannington GSP 132kV CBs reinforcemen | 132/33 | Amber
LYTCHETT | MANNINGTON GSP | 11.08/25.0 | 50.747525 | -2.032591 | 90.00 | 0.00 | 17.50 | 68.32 | 94.83 | 0.00 |  | Constrained |  |  | Constrained | Update protection settings. | 01/04/2021 | Yes | Yes | BSP Transfomer rating limitation under N-1,Any new connection will trigger Mannington GSP 132kV CBs reinforcemen,Any new connection will trigger Mannington GSP 132kV CBs reinforcemen | 132/33 | Red
MANNINGTON | MANNINGTON GSP | 11.68/13.1 | 50.846472 | -1.894513 | 120.00 | 0.00 | 19.59 | 122.25 | 120.92 | 0.00 |  | Constrained |  |  | Constrained | Reinf 33kV isolators on the Mannington/Mill Lane, AVC reinforcement. | 01/12/2021 | Yes | Yes | BSP Transfomer rating limitation under N-1 | 132/33 | Red
POOLE PS (HAMWORTHY) | MANNINGTON GSP | 13.89/25.0 | 50.714966 | -1.985812 | 60.00 | 0.00 | 11.10 | 32.50 | 3.40 | 0.00 |  | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Any new connection will trigger Mannington GSP 132kV CBs reinforcemen | 132/33 | Amber
REDHILL | MANNINGTON GSP | 19.19/25 | 50.764994 | -1.879694 | 90.00 | 0.00 | 15.65 | 61.73 | 76.98 | 34.60 |  | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Any new connection will trigger Mannington GSP 132kV CBs reinforcemen | 132/33 | Amber
SALISBURY | MANNINGTON GSP | 20.5/25.0 | 51.081780 | -1.843629 | 105.00 | 0.00 | 16.14 | 102.08 | 29.60 | 0.00 |  | Constrained |  |  | Constrained |  |  | Yes | Yes | BSP Transfomer rating limitation under N-1,Any new connection will trigger Mannington GSP 132kV CBs reinforcemen,Any new connection will trigger Mannington GSP 132kV CBs reinforcemen | 132/33 | Red
SHAFTESBURY | MANNINGTON GSP | 16.1/25.0 | 51.013374 | -2.208783 | 90.00 | 0.00 | 10.37 | 75.77 | 86.64 | 0.00 |  | Constrained |  |  | Constrained | AVC reinforcement | 01/12/2021 | Yes | Yes | BSP Transfomer rating limitation under N-1 | 132/33 | Red
WAREHAM | MANNINGTON GSP | 12.9/13.1 | 50.695642 | -2.121044 | 30.00 | 0.00 | 7.38 | 30.06 | 48.09 | 0.00 |  | Constrained |  |  | Constrained | AVC reinforcement | 01/12/2021 | Yes | Yes | BSP Transfomer rating limitation under N-1,Any new connection will trigger Mannington GSP 132kV CBs reinforcemen,Any new connection will trigger Mannington GSP 132kV CBs reinforcemen | 132/33 | Red
WINFRITH HEATH | MANNINGTON GSP | 15.68/17.5 | 50.678188 | -2.273824 | 30.00 | 0.00 | 0.68 | 6.28 | 21.87 | 0.00 |  | Constrained |  |  | Constrained | Update protection settings. | 01/10/2020 | Yes | Yes | Any new connection will trigger Mannington GSP 132kV CBs reinforcemen | 132/11 | Red
ANDOVER | MELKSHAM | 12.35/17.5 | 51.217503 | -1.495504 | 90.00 | 36.83 | 23.20 | 86.00 | 113.90 | 0.60 |  | Constrained |  |  | Constrained | Andover-Amesbury reconfiguration. Switchgear reinforcement. | 31/12/2021 | Yes | No | BSP and upstream 132kV system capacity saturated. | 132/33 | Red
CHIPPENHAM | MELKSHAM | 20.2/25 | 51.467403 | -2.107143 | 180.00 | 63.15 | 25.60 | 94.70 | 217.30 | 1.26 |  | Partially Constrained |  |  | Constrained | Switchgear-C, AVC, load blinder reinforcements. Malmesbury - Rodbourne Rail tee OHL reinforcement. To install thired BSP transformer | 01/06/2022 | Yes | No | Constrained due to BSP transformers limitations under FCO. | 132/33 | Red
FROME | MELKSHAM | 19.92/25.0 | 51.231041 | -2.304881 | 90.00 | 21.05 | 29.50 | 110.30 | 154.20 | 0.00 |  | Constrained |  |  | Unconstrained | AVC & Load Blinder. Frome-C switchgear reinforcement (Fl results include new rating) | 01/12/2021 | Yes | No | BSP capacity saturated. | 132/33 | Red
NORRINGTON | MELKSHAM | 24.6/31.5 | 51.383779 | -2.169901 | 270.00 | 0.00 | 38.10 | 210.50 | 250.50 | 53.60 |  | Unconstrained |  |  | Constrained | NORR-CORS 33kV cable upgrade. | 01/10/2021 | Yes | No | Existing headroom for the BSP however downstream 33kV system is constrained. | 132/33 | Green
WEST GRAFTON | MELKSHAM | 12.48/17.5 | 51.331515 | -1.652557 | 45.00 | 0.00 | 9.20 | 9.20 | 5.82 | 0.60 |  | Constrained |  |  | Unconstrained |  |  | Yes | No | Proximity to voltage issues near Malmesbury. | 132/33 | Red
CIRENCESTER | MINETY | 15.49/25 | 51.702336 | -1.962764 | 90.00 | 64.21 | 12.10 | 54.13 | 110.70 | 6.34 |  | Partially Constrained |  |  | Unconstrained | AVC and Load blinder reinforcement. | 01/06/2022 | Yes | Yes | Future connections on Minety GSP will need ANM under N-2, due to NG SGT constraints. | 132/33 | Amber
GALILEO | MINETY | 19.35/25 | 51.552396 | -1.848441 | 45.00 | 0.00 | 8.10 | 29.20 | 10.00 | 0.00 |  | Constrained |  |  | Unconstrained |  |  | Yes | Yes | National Grid reinforcement works required for saturated N-1 SGT capacity, estimated connection date for new applications is 2025-2026. | 132/11 | Red
STRATTON MAIN | MINETY | 15.05/17.5 | 51.597158 | -1.754525 | 90.00 | 21.05 | 20.50 | 95.40 | 90.10 | 0.00 |  | Constrained |  |  | Partially Constrained | Load blinder reinforcement | 01/12/2020 | Yes | Yes | National Grid reinforcement works required for saturated N-1 SGT capacity, estimated connection date for new applications is 2025-2026. | 132/33 | Red
STRATTON RESERVE | MINETY | 18.94/25.0 | 51.597157 | -1.754524 | 60.00 | 0.00 | 14.60 | 59.40 | 49.10 | 0.00 |  | Constrained |  |  | Partially Constrained |  |  | Yes | Yes | National Grid reinforcement works required for saturated N-1 SGT capacity, estimated connection date for new applications is 2025-2026. | 132/33 | Red
SWINDON | MINETY | 16.78/17.5 | 51.580000 | -1.821600 | 90.00 | 0.00 | 19.90 | 79.40 | 84.70 | 0.00 |  | Constrained |  |  | Constrained |  | 01/01/2022 | Yes | Yes | National Grid reinforcement works required for saturated N-1 SGT capacity, estimated connection date for new applications is 2025-2026. | 132/33 | Red
TOOTHILL | MINETY | 18.83/25.0 | 51.554239 | -1.811136 | 90.00 | 0.00 | 17.00 | 86.20 | 108.27 | 0.00 |  | Constrained |  |  | Constrained | Load blinder reinforcement, Toothill-C switchgear upgrade (FL results include new rating) | 01/10/2021 | Yes | Yes | National Grid reinforcement works required for saturated N-1 SGT capacity, estimated connection date for new applications is 2025-2026. | 132/33 | Red
HAYES | NORTH HYDE | 15.96/17.5 | 51.504201 | -0.423455 | 60.00 | 0.00 | 23.40 | 58.50 | 0.00 | 74.60 |  | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/11 | Green
NORTH HYDE (D) | NORTH HYDE | 7.78/18.4 | 51.498458 | -0.411681 | 45.00 | 0.00 | 13.10 | 41.00 | 0.00 | 49.90 |  | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/22 | Green
NORTH HYDE (E) | NORTH HYDE | 11.06/13.1 | 51.498458 | -0.411681 | 76.00 | 0.00 | 29.10 | 67.80 | 0.00 | 54.10 |  | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/11 | Green
VICARAGE FARM ROAD | NORTH HYDE | 12.58/13.1 | 51.475737 | -0.383556 | 38.00 | 0.00 | 8.01 | 27.75 | 0.00 | 0.70 |  | Unconstrained |  |  | Partially Constrained |  |  | No | No | Moderate proximity to fault rating | 66/11 | Amber
ROWNHAMS | NURSLING | 19.08/25 | 50.949937 | -1.472239 | 90.00 | 0.00 | 28.25 | 101.51 | 106.91 | 10.00 |  | Unconstrained |  |  | Partially Constrained | Rownhams-C switchgear reinforcement (FL Results include new rating), Directional Relay Reinforcement | 01/10/2021 | No | Yes | No spare bay AND/OR space for extension | 132/33 | Amber
SOUTHAMPTON MAIN | NURSLING | 11.01/13.1 | 50.905983 | -1.412221 | 90.00 | 0.00 | 18.50 | 69.90 | 1.20 | 61.60 |  | Unconstrained |  |  | Partially Constrained |  |  | No | Yes | AVC reinforcement to be triggered | 132/33 | Amber
SOUTHAMPTON RESERVE | NURSLING | 11.09/17.5 | 50.906351 | -1.412145 | 90.00 | 0.00 | 12.81 | 55.31 | 8.81 | 82.10 |  | Unconstrained |  |  | Partially Constrained |  |  | No | Yes | AVC reinforcement to be triggered | 132/33 | Amber
VELMORE | NURSLING | 13.28/17.5 | 50.970247 | -1.393579 | 90.00 | 0.00 | 24.59 | 96.40 | 31.72 | 83.40 |  | Unconstrained |  |  | Constrained |  |  | No | Yes | Proximity to fault rating | 132/33 | Red
WINCHESTER | NURSLING | 15.58/25.0 | 51.037645 | -1.359982 | 90.00 | 0.00 | 22.73 | 101.40 | 60.00 | 0.70 |  | Unconstrained |  |  | Partially Constrained |  |  | No | Yes | No spare bay AND/OR space for extension, long interactivity queue | 132/33 | Amber
ACTON LANE | WILLESDEN | 12.06/19.7 | 51.534071 | -0.259208 | 156.00 | 0.00 | 8.50 | 33.02 | 0.00 | 48.50 |  | Constrained |  |  | Constrained | Andover-Amesbury reconfiguration. Switchgear reinforcement. |  | Yes | No | None known | 66/22 | Red
GREENFORD | WILLESDEN | 17.54/25 | 51.541366 | -0.347617 | 60.00 | 0.00 | 14.90 | 45.87 | 0.00 | 74.40 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 66/11 | Green
PERIVALE | WILLESDEN | 13.48/25 | 51.533202 | -0.306749 | 40.00 | 0.00 | 9.54 | 28.84 | 0.00 | 49.50 |  | Unconstrained |  |  | Partially Constrained |  |  | Yes | No | Moderate proximity to fault rating | 66/11 | Amber

## PSS
Primary Substation Name | Corresponding GSP | Corresponding BSP | Break Fault level vs Rating (kA) | Latitude | Longitude | Transformer Nameplate Rating (MVA) | Sum of Quoted Generation (MVA) | Minimum Load (MW) | Maximum Load (MW) | Contracted Generation (MVA) | Available Headroom Capacity (MVA) | Reverse Powerflow Capability (%) | Upstream Status | Transmission Works | Transmission Reinforcement Completion Date | Downstream Status | Distribution Works | Distribution Reinforcement Completion Date | SoW Needed? | Part of SWAN? | Other Constraints | Voltage (kV) | Site Classification
HILLINGDON | IVER 66KV |  | 13.14/25.0 | 51.534162 | -0.452395 | 40.00 | 0.00 | 10.24 | 31.79 | 0.00 | 50.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/11 | Green
NORTHOLT | IVER 66KV |  | 11.84/13.1 | 51.537051 | -0.393035 | 38.00 | 0.00 | 6.00 | 29.35 | 0.00 | 44.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/11 | Green
UXBRIDGE | IVER 66KV |  | 10.33/20.0 | 51.541092 | -0.487346 | 72.80 | 0.00 | 11.71 | 49.79 | 0.00 | 84.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/11 | Green
YIEWSLEY | IVER 66KV |  | 10.53/13.1 | 51.517607 | -0.479188 | 60.00 | 0.00 | 8.42 | 39.86 | 0.00 | 68.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/11 | Green
BOWERDEAN |  | LOUDWATER | 10.27/13.1 | 51.636442 | -0.733444 | 26.00 | 0.00 | 3.94 | 20.41 | 0.00 | 29.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
FLACKWELL HEATH |  | LOUDWATER | 11.45/13.1 | 51.596255 | -0.692982 | 26.70 | 0.00 | 2.22 | 20.54 | 1.40 | 27.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
WELL END |  | LOUDWATER | 8.68/13.1 | 51.583638 | -0.723077 | 24.00 | 0.00 | 4.13 | 21.16 | 7.20 | 20.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
WYCOMBE MARSH |  | LOUDWATER | 8.0/25.0 | 51.618418 | -0.721379 | 17.30 | 0.00 | 2.21 | 10.61 | 0.00 | 19.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
CASTLE CARY |  | YEOVIL | 5.67/25.0 | 51.077697 | -2.507499 | 15.00 | 7.50 | 1.10 | 5.93 | 5.12 | 7.00 | 50 | Constrained |  |  | Unconstrained |  |  | No | Yes | Moderate proximity to upstream 33kV circts restrictions. There is no reverse power capacity at the Yeovil BSP, 33kV circuit thermal limitation. | 33/11 | Red
CHILTON CANTELO |  | YEOVIL | 7.83/20.0 | 50.992247 | -2.601376 | 9.75 | 0.00 | 2.47 | 11.22 | 0.00 | 12.00 | 50 | Constrained |  |  | Unconstrained |  |  | No | Yes | Moderate proximity to upstream 33kV circts restrictions.There is no reverse power capacity at the Yeovil BSP,33kV circuit thermal limitation. | 33/11 | Red
HENSTRIDGE |  | YEOVIL | 3.92/25.0 | 50.972734 | -2.389480 | 24.00 | 0.00 | 0.96 | 8.51 | 4.23 | 20.00 | 50 | Constrained |  |  | Unconstrained |  |  | No | Yes | Moderate Proximity to thermal rating on short section of 132kV circt Axminster-Yeovil under FCO,There is no reverse power capacity at the Yeovil BSP | 33/11 | Red
LARKHILL |  | YEOVIL | 9.57/25.0 | 50.950109 | -2.661191 | 23.00 | 0.00 | 2.53 | 13.42 | 0.00 | 25.00 | 50 | Constrained |  |  | Unconstrained |  |  | No | Yes | Moderate Proximity to thermal rating on short section of 132kV circt Axminster-Yeovil under FCO,There is no reverse power capacity at the Yeovil BSP | 33/11 | Red
MILBORNE PORT |  | YEOVIL | 2.49/13.1 | 50.976706 | -2.459307 | 3.50 | 0.00 | 0.59 | 3.87 | 4.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations.There is no reverse power capacity at the Yeovil BSP | 33/11 | Red
PULHAM |  | YEOVIL | 4.4/13.1 | 50.883477 | -2.404798 | 5.00 | 0.00 | 0.78 | 4.34 | 0.00 | 7.00 | 50 | Constrained |  |  | Unconstrained |  |  | No | Yes | Moderate Proximity to thermal rating on short section of 132kV circt Axminster-Yeovil under FCO,There is no reverse power capacity at the Yeovil BSP | 33/11 | Red
SHERBORNE |  | YEOVIL | 7.55/13.1 | 50.962449 | -2.514273 | 10.00 | 0.00 | 2.19 | 8.44 | 0.00 | 7.00 | 50 | Constrained |  |  | Partially Constrained |  |  | No | Yes | Limited expansion space for CB connections,There is no reverse power capacity at the Yeovil BSP | 33/11 | Red
SPARKFORD |  | YEOVIL | 6.88/13.1 | 51.027340 | -2.560621 | 5.00 | 0.00 | 0.85 | 3.44 | 0.20 | 7.00 | 50 | Constrained |  |  | Unconstrained |  |  | No | Yes | Moderate Proximity to thermal rating on short section of 132kV circt Axminster-Yeovil under FCO,There is no reverse power capacity at the Yeovil BSP | 33/11 | Red
WEST HENDFORD |  | YEOVIL | 12.38/13.1 | 50.936725 | -2.642500 | 30.00 | 0.00 | 5.63 | 19.85 | 0.00 | 7.00 | 50 | Constrained |  |  | Partially Constrained |  |  | No | Yes | Moderate Proximity to thermal rating on short section of 132kV circt Axminster-Yeovil under FCO. Moderate proximity to fault rating,There is no reverse power capacity at the Yeovil BSP | 33/11 | Red
YEOVIL |  | YEOVIL | 13.18/25 | 50.949910 | -2.605157 | 20.00 | 0.00 | 2.70 | 15.55 | 10.00 | 7.00 | 50 | Constrained |  |  | Unconstrained | Yeovil-E switchgear reinforcement (completed - FL results include new rating). |  | No | Yes | Moderate Proximity to thermal rating on short section of 132kV circt Axminster-Yeovil under FCO,There is no reverse power capacity at the Yeovil BSP | 33/11 | Red
YETMINSTER |  | YEOVIL | 8.06/25.0 | 50.890804 | -2.567226 | 7.50 | 0.00 | 1.52 | 7.10 | 0.80 | 7.00 | 50 | Constrained |  |  | Partially Constrained |  |  | No | Yes | Moderate Proximity to thermal rating on short section of 132kV circt Axminster-Yeovil under FCO,There is no reverse power capacity at the Yeovil BSP | 33/11 | Red
PARK GATE |  | BOTLEY WOOD | 8.27/13.1 | 50.871476 | -1.271319 | 30.00 | 0.00 | 4.41 | 21.57 | 0.00 | 27.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
WHITELEY |  | BOTLEY WOOD | 8.52/25.0 | 50.876464 | -1.249637 | 30.00 | 0.00 | 6.56 | 25.70 | 0.00 | 27.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
BISHOPS WALTHAM |  | NETLEY COMMON | 7.42/20.0 | 50.946416 | -1.194135 | 24.00 | 0.00 | 3.17 | 15.58 | 7.50 | 19.00 | 50 | Partially Constrained |  |  | Unconstrained |  |  | No | Yes | 33kV upstream restriction on Netley Common to Bishops Waltham 33kV circts | 33/11 | Amber
BITTERNE |  | NETLEY COMMON | 8.24/25.0 | 50.964778 | -1.340207 | 13.00 | 0.00 | 1.69 | 9.73 | 0.00 | 14.00 | 50 | Partially Constrained |  |  | Unconstrained |  |  | No | Yes | Proximity to voltage issues. | 33/6.6 | Amber
HAMBLE |  | NETLEY COMMON | 10.62/20.0 | 50.876493 | -1.328094 | 30.00 | 7.60 | 6.86 | 16.89 | 12.20 | 24.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
NETLEY COMMON 11KV |  | NETLEY COMMON | 12.25/13.1 | 50.905547 | -1.324988 | 30.00 | 0.00 | 5.88 | 26.65 | 0.00 | 34.60 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
TOWNHILL PARK |  | NETLEY COMMON | 8.45/13.1 | 50.930800 | -1.358760 | 30.00 | 0.00 | 4.64 | 20.05 | 0.00 | 34.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
WESTON |  | NETLEY COMMON | 10.81/13.1 | 50.887006 | -1.358650 | 26.00 | 0.00 | 1.36 | 10.55 | 2.60 | 25.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
WOOLSTON |  | NETLEY COMMON | 7.45/20.0 | 50.898687 | -1.373563 | 16.90 | 0.00 | 4.55 | 16.83 | 0.00 | 21.00 | 50 | Partially Constrained |  |  | Unconstrained |  |  | No | Yes | Proximity to voltage issues. | 33/6.6 | Amber
BOSCOMBE DOWN |  | AMESBURY | 10.09/13.1 | 51.168258 | -1.755519 | 30.00 | 0.00 | 6.21 | 24.05 | 14.00 | 22.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Connections might not be possible prior to Andover-Amesbury reconfiguration scheme. | 33/11 | Amber
ENFORD |  | AMESBURY | 4.05/25.0 | 51.264746 | -1.805745 | 8.00 | 0.00 | 0.43 | 3.84 | 0.00 | 8.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to Primary transformers limitations. Connections might not be possible prior to Andover-Amesbury reconfiguration scheme. | 33/11 | Red
PARK HOUSE |  | AMESBURY | 4.3/25.0 | 51.192866 | -1.669957 | 4.00 | 0.00 | 0.21 | 2.01 | 0.00 | 4.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to Primary transformers limitations. Connections might not be possible prior to Andover-Amesbury reconfiguration scheme. | 33/11 | Red
PEWSEY |  | AMESBURY | 2.84/25.0 | 51.333058 | -1.791103 | 17.00 | 0.00 | 1.17 | 8.89 | 0.00 | 17.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Connections might not be possible prior to Andover-Amesbury reconfiguration scheme. | 33/11 | Amber
BALL HILL |  | THATCHAM | 5.88/13.1 | 51.367632 | -1.391608 | 15.00 | 0.00 | 1.20 | 6.03 | 0.00 | 16.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
BEENHAM |  | THATCHAM | 6.52/13.1 | 51.417451 | -1.159422 | 13.00 | 0.00 | 1.41 | 6.88 | 1.90 | 7.50 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
GREENHAM COMMON |  | THATCHAM | 8.29/25.0 | 51.424693 | -1.000632 | 24.00 | 0.00 | 2.48 | 7.35 | 0.00 | 26.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
HUNGERFORD |  | THATCHAM | 5.83/13.1 | 51.419447 | -1.511721 | 13.00 | 0.00 | 1.81 | 8.75 | 0.00 | 0.00 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | No | None known | 33/11 | Red
KINGSCLERE |  | THATCHAM | 6.75/25.0 | 51.330881 | -1.255738 | 9.80 | 0.00 | 1.45 | 6.30 | 0.00 | 11.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
KINTBURY |  | THATCHAM | 5.9/13.1 | 51.403036 | -1.460143 | 10.00 | 0.00 | 1.09 | 5.49 | 0.20 | 10.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
LAMBOURN |  | THATCHAM | 5.7/25.0 | 51.501726 | -1.521778 | 9.80 | 0.00 | 1.53 | 7.88 | 0.00 | 11.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
LECKHAMPSTEAD |  | THATCHAM | 4.52/13.1 | 51.496090 | -1.368293 | 6.50 | 0.00 | 0.61 | 5.06 | 0.00 | 7.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
LOVE LANE |  | THATCHAM | 8.85/25.0 | 51.413999 | -1.320535 | 40.00 | 0.00 | 6.43 | 21.75 | 0.00 | 46.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
RIVERSIDE |  | THATCHAM | 12.11/20.0 | 51.403168 | -1.313507 | 22.90 | 0.00 | 2.68 | 12.68 | 0.00 | 25.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ST JOHNS |  | THATCHAM | 10.52/13.1 | 51.394474 | -1.324489 | 25.30 | 0.00 | 0.15 | 22.18 | 0.00 | 25.00 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | No | Constrained due to Primary transformers limitations. | 33/11 | Red
TADLEY |  | THATCHAM | 7.61/25.0 | 51.359992 | -1.171964 | 15.20 | 0.00 | 1.84 | 8.67 | 0.30 | 0.00 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | No | No spare bay. | 33/11 | Red
THATCHAM |  | THATCHAM | 14.81/25.0 | 51.394501 | -1.242144 | 30.00 | 0.00 | 6.13 | 23.62 | 11.30 | 24.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
YATTENDON |  | THATCHAM | 5.99/12.0 | 51.465576 | -1.227638 | 13.00 | 0.00 | 2.27 | 10.27 | 0.00 | 15.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
BASINGSTOKE |  | BASINGSTOKE T1A & T2A | 11.15/13.1 | 51.269829 | -1.067768 | 30.00 | 0.00 | 0.88 | 19.90 | 12.75 | 18.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
JAYS CLOSE |  | BASINGSTOKE T1A & T2A | 14.08/20.0 | 51.246407 | -1.097842 | 40.00 | 0.00 | 7.26 | 22.42 | 4.00 | 33.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ARBORFIELD |  | BASINGSTOKE T1B & T2B | 4.34/13.1 | 51.398309 | -0.909654 | 18.00 | 0.00 | 2.25 | 14.87 | 2.44 | 17.00 | 50 | Unconstrained |  |  | Partially Constrained |  |  | Yes | No | Connections might not be possible prior to Bramley Green-Arborfield reconfiguration. | 33/11 | Amber
BRAMLEY GREEN |  | BASINGSTOKE T1B & T2B | 6.05/25.0 | 51.321708 | -1.033883 | 15.00 | 0.00 | 1.19 | 4.49 | 0.00 | 16.00 | 50 | Unconstrained |  |  | Partially Constrained |  |  | Yes | No | Connections might not be possible prior to Bramley Green-Arborfield reconfiguration. | 33/11 | Amber
CHINEHAM |  | BASINGSTOKE T1B & T2B | 9.01/25.0 | 51.299452 | -1.072648 | 30.00 | 0.00 | 3.72 | 16.42 | 1.37 | 32.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
DOWN GRANGE |  | BASINGSTOKE T1B & T2B | 9.30/13.1 | 51.247932 | -1.119819 | 30.00 | 0.00 | 3.90 | 21.05 | 0.00 | 18.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
OVERTON |  | BASINGSTOKE T1B & T2B | 9.58/13.1 | 51.254628 | -1.255537 | 16.00 | 0.00 | 1.61 | 13.36 | 11.60 | 6.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
BROOK STREET |  | BASINGSTOKE T3 & T4 | 9.81/13.1 | 51.265698 | -1.091244 | 30.00 | 0.00 | 3.53 | 14.71 | 0.00 | 33.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
HOUNDMILLS |  | BASINGSTOKE T3 & T4 | 9.72/25.0 | 51.271327 | -1.110055 | 40.00 | 0.00 | 6.43 | 18.03 | 2.50 | 43.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
OAKRIDGE |  | BASINGSTOKE T3 & T4 | 7.94/13.1 | 51.278728 | -1.090270 | 30.00 | 0.00 | 2.16 | 9.73 | 0.00 | 32.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
CERNE ABBAS |  | CHICKERELL | 1.32/13.1 | 50.807863 | -2.481776 | 2.60 | 0.00 | 1.00 | 1.64 | 0.00 | 3.00 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Constrained due to Primary transformers limitations.There is no reverse power capacity at the Chickerell BSP | 33/11 | Red
CHARMINSTER |  | CHICKERELL | 5.95/25.0 | 50.737037 | -2.464043 | 12.00 | 0.00 | 1.90 | 9.44 | 0.00 | 14.00 | 50 | Constrained |  |  | Unconstrained |  |  | No | Yes | There is no reverse power capacity at the Chickerell BSP | 33/11 | Amber
CHICKERELL |  | CHICKERELL | 9.48/25.0 | 50.623078 | -2.488720 | 14.80 | 0.00 | 2.00 | 8.06 | 4.77 | 10.00 | 50 | Constrained |  |  | Unconstrained |  |  | No | Yes | There is no reverse power capacity at the Chickerell BSP | 33/11 | Amber
DORCHESTER |  | CHICKERELL | 8.33/13.0 | 50.712856 | -2.438310 | 21.00 | 0.00 | 5.00 | 19.59 | 2.00 | 3.00 | 50 | Constrained |  |  | Unconstrained |  |  | No | Yes | Upstream 33kV circts restrictions under FCO. Potential Voltage issue for new connections.There is no reverse power capacity at the Chickerell BSP | 33/11 | Red
MAIDEN NEWTON |  | CHICKERELL | 6.49/25.0 | 51.384730 | -0.593779 | 10.00 | 0.00 | 1.90 | 8.79 | 0.00 | 14.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | There is no reverse power capacity at the Chickerell BSP | 33/11 | Amber
PIDDLETRENTHIDE |  | CHICKERELL | 5.37/13.1 | 50.797437 | -2.424912 | 5.00 | 0.00 | 0.32 | 2.67 | 0.00 | 6.00 | 50 | Constrained |  |  | Partially Constrained |  |  | No | Yes | Moderate proximity to Primary transformers limitations.There is no reverse power capacity at the Chickerell BSP | 33/11 | Amber
PORTLAND |  | CHICKERELL | 8.70/13.1 | 50.564428 | -2.450344 | 18.10 | 0.00 | 2.80 | 10.72 | 2.40 | 18.00 | 50 | Constrained |  |  | Unconstrained |  |  | No | Yes | There is no reverse power capacity at the Chickerell BSP | 33/11 | Amber
PUDDLETOWN |  | CHICKERELL | 4.49/13.1 | 50.754916 | -2.367821 | 6.30 | 0.00 | 0.47 | 2.62 | 0.00 | 6.00 | 50 | Constrained |  |  | Partially Constrained |  |  | No | Yes | Moderate proximity to Primary transformers limitations.There is no reverse power capacity at the Chickerell BSP | 33/11 | Amber
REDLANDS |  | CHICKERELL | 9.36/13.1 | 50.639011 | -2.465198 | 15.00 | 0.00 | 2.23 | 11.13 | 0.00 | 17.00 | 50 | Constrained |  |  | Unconstrained |  |  | No | Yes | There is no reverse power capacity at the Chickerell BSP | 33/11 | Amber
WEYMOUTH |  | CHICKERELL | 12.73/20.0 | 50.611154 | -2.459976 | 30.00 | 0.00 | 7.30 | 24.66 | 3.02 | 23.00 | 50 | Constrained |  |  | Unconstrained |  |  | No | Yes | There is no reverse power capacity at the Chickerell BSP | 33/11 | Amber
COWLEY LOCAL |  | COWLEY LOCAL MAIN | 11.14/25.0 | 51.724729 | -1.190222 | 30.00 | 0.00 | 5.94 | 24.32 | 0.71 | 35.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ROSE HILL |  | COWLEY LOCAL MAIN | 10.95/13.1 | 51.723613 | -1.224698 | 26.00 | 0.00 | 3.83 | 17.68 | 0.80 | 29.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
UNION STREET |  | COWLEY LOCAL MAIN | 9.84/25.0 | 51.749582 | -1.235987 | 30.00 | 0.00 | 4.48 | 16.88 | 0.00 | 34.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
BERINSFIELD |  | COWLEY LOCAL RESERVE | 7.76/20.0 | 51.654638 | -1.157790 | 24.00 | 0.00 | 1.33 | 11.80 | 6.14 | 19.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | Moderate proximity to 33kV circt limits under FCO. | 33/11 | Green
KENNINGTON |  | COWLEY LOCAL RESERVE | 4.30/13.1 | 51.706153 | -1.235850 | 6.00 | 0.00 | 0.69 | 4.45 | 0.40 | 6.00 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | No | Limited space for extension. | 33/11 | Red
WALLINGFORD |  | COWLEY LOCAL RESERVE | 7.61/13.1 | 51.600806 | -1.136695 | 19.50 | 0.00 | 3.87 | 16.02 | 4.49 | 18.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | Moderate proximity to 33kV circt limits under FCO. | 33/11 | Green
CHOLSEY |  | DRAYTON | 5.75/13.1 | 51.557821 | -1.160733 | 15.00 | 0.00 | 1.25 | 7.77 | 0.30 | 7.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constrained due to 33kV circts limitations under FCO. | 33/11 | Red
FULSCOT |  | DRAYTON | 10.73/13.1 | 51.601452 | -1.215950 | 21.00 | 0.00 | 2.85 | 15.99 | 7.56 | 7.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constrained due to 33kV circts limitations under FCO. | 33/11 | Red
GROVE |  | DRAYTON | 7.23/13.1 | 51.603408 | -1.430626 | 15.00 | 0.00 | 4.96 | 19.99 | 0.00 | 7.00 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | No | Limited space for extension. | 33/11 | Red
MILTON |  | DRAYTON | 15.49/16.0 | 50.849556 | -1.793267 | 46.40 | 0.00 | 9.83 | 36.92 | 6.84 | 7.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
WANTAGE |  | DRAYTON | 9.40/13.1 | 51.592043 | -1.405217 | 19.50 | 0.00 | 1.97 | 15.01 | 0.05 | 7.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
WINSMORE LANE |  | DRAYTON | 10.25/13.1 | 51.668696 | -1.284487 | 26.00 | 0.00 | 4.11 | 17.13 | 0.00 | 7.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ARNCOTT |  | HEADINGTON | 9.24/13.1 | 51.857927 | -1.120313 | 15.00 | 0.00 | 1.93 | 7.39 | 12.20 | 1.00 | 50 | Constrained |  |  | Unconstrained | Headington reconfiguration | 01/03/20 | Yes | No | Voltage & thermal upstream limitations. | 33/11 | Red
HEADINGTON |  | HEADINGTON | 13.81/25.0 | 51.768486 | -1.212191 | 40.00 | 0.00 | 4.10 | 20.03 | 3.60 | 11.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | Voltage constraints. | 33/11 | Green
OLD ROAD |  | HEADINGTON | 10.83/13.1 | 51.753837 | -1.199842 | 30.00 | 0.00 | 6.69 | 15.66 | 0.34 | 11.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
WHEATLEY |  | HEADINGTON | 8.9/16.0 | 51.744015 | -1.121223 | 15.00 | 0.00 | 2.69 | 8.27 | 7.12 | 11.00 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | No | Limited space for extension. | 33/11 | Red
CHISBRIDGE |  | HIGH WYCOMBE | 6.32/13.1 | 51.595327 | -0.842663 | 9.80 | 0.00 | 1.80 | 5.57 | 0.00 | 1.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Limited expansion space for CB connections. Upstream Voltage & thermal issues. | 33/11 | Red
FRYERS LANE |  | HIGH WYCOMBE | 11.8/13.1 | 51.637149 | -0.774608 | 26.00 | 0.00 | 2.82 | 13.39 | 0.00 | 21.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
HIGH WYCOMBE |  | HIGH WYCOMBE | 9.01/13.1 | 51.621698 | -0.776035 | 30.00 | 0.00 | 6.12 | 21.99 | 1.07 | 21.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | Voltage constraints. | 33/11 | Green
HIGH WYCOMBE TOWN |  | HIGH WYCOMBE | 13.18/13.1 | 51.636444 | -0.733588 | 46.30 | 0.00 | 6.66 | 28.45 | 0.00 | 21.00 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | No | Proximity to fault rating | 33/11 | Red
LITTLE MARLOW |  | HIGH WYCOMBE | 7.78/20.0 | 51.580688 | -0.758230 | 30.00 | 0.00 | 5.00 | 17.57 | 0.00 | 21.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
NUFFIELD |  | HIGH WYCOMBE | 3.47/25.0 | 51.576213 | -1.016520 | 7.00 | 0.00 | 0.78 | 4.10 | 0.00 | 1.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | Upstream Voltage & thermal issues. | 33/11 | Red
STOKENCHURCH |  | HIGH WYCOMBE | 6.53/20.0 | 51.646845 | -0.890696 | 9.80 | 0.00 | 1.98 | 9.20 | 0.00 | 1.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Upstream Voltage & thermal issues. | 33/11 | Red
WATLINGTON |  | HIGH WYCOMBE | 5.72/25.0 | 51.642992 | -1.002503 | 9.80 | 0.00 | 1.40 | 5.81 | 17.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Upstream Voltage & thermal issues. | 33/11 | Red
FRENCHAY ROAD |  | OXFORD | 10.28/13.1 | 51.770661 | -1.270558 | 19.50 | 0.00 | 2.35 | 10.94 | 0.00 | 11.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
NORTH HINKSEY |  | OXFORD | 7.11/25.0 | 51.735490 | -1.297625 | 9.80 | 0.00 | 1.45 | 7.16 | 1.30 | 9.00 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | No | No spare bay. | 33/11 | Red
OSNEY |  | OXFORD | 9.26/13.1 | 51.749564 | -1.275823 | 30.00 | 0.00 | 5.99 | 23.60 | 0.50 | 11.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ST EBBES |  | OXFORD | 10.39/25.0 | 51.748156 | -1.259100 | 30.00 | 0.00 | 5.33 | 21.84 | 0.70 | 11.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
WOOTTON ROAD |  | OXFORD | 6.63/25.0 | 51.680859 | -1.288635 | 18.20 | 0.00 | 2.88 | 13.21 | 0.24 | 11.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
BLEDINGTON |  | WITNEY & YARNTON | 3.03/25.0 | 51.772067 | -1.485304 | 5.00 | 0.00 | 1.20 | 4.29 | 0.19 | 3.00 | 50 | Constrained |  |  | Partially Constrained |  |  | Yes | No | Moderate proximity to Primary transformers limitations under FCO. | 33/11 | Red
BURFORD |  | WITNEY & YARNTON | 5.84/13.1 | 51.810546 | -1.627900 | 6.50 | 0.00 | 0.76 | 4.79 | 0.00 | 3.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Limited expansion space for CB connections | 33/11 | Red
CARTERTON |  | WITNEY & YARNTON | 8.91/13.1 | 51.768079 | -1.591876 | 30.00 | 0.00 | 4.95 | 20.56 | 0.00 | 3.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Limited expansion space for CB connections. | 33/11 | Red
CHARLBURY |  | WITNEY & YARNTON | 6.39/13.1 | 51.863020 | -1.477166 | 15.00 | 0.00 | 1.20 | 5.13 | 4.38 | 3.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Limited expansion space for CB connections | 33/11 | Red
CHIPPING NORTON |  | WITNEY & YARNTON | 5.53/25.0 | 51.938375 | -1.544658 | 15.00 | 0.00 | 3.35 | 10.26 | 0.05 | 3.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constrained due to upstream thermal and voltage issues. | 33/11 | Red
DEDDINGTON |  | WITNEY & YARNTON | 3.87/13.1 | 51.969031 | -1.320182 | 4.00 | 0.00 | 0.90 | 4.51 | 0.05 | 3.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to upstream thermal and voltage issues. | 33/11 | Red
EYNSHAM |  | WITNEY & YARNTON | 6.82/25.0 | 51.789495 | -1.388416 | 24.00 | 0.00 | 3.69 | 11.81 | 1.00 | 3.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Limited expansion space for CB connections | 33/11 | Red
FYFIELD |  | WITNEY & YARNTON | 4.83/25.0 | 51.693298 | -1.390147 | 15.00 | 0.00 | 1.71 | 8.89 | 0.00 | 3.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constrained due to upstream thermal limitations. | 33/11 | Red
KIDDINGTON |  | WITNEY & YARNTON | 6.2/13.1 | 51.915101 | -1.371446 | 24.00 | 0.00 | 2.64 | 11.31 | 0.18 | 3.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Voltage constraints. | 33/11 | Red
LEAFIELD |  | WITNEY & YARNTON | 6.15/13.1 | 51.835044 | -1.561665 | 6.50 | 0.00 | 0.82 | 3.55 | 0.00 | 3.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Voltage constraints. | 33/11 | Red
LOVELACE ROAD |  | WITNEY & YARNTON | 4.74/13.1 | 51.789722 | -1.270541 | 12.00 | 0.00 | 1.19 | 5.21 | 0.00 | 3.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Single security Primary. | 33/11 | Red
RISSINGTON |  | WITNEY & YARNTON | 3.07/16.0 | 51.874373 | -1.722081 | 10.30 | 0.00 | 1.40 | 6.72 | 0.00 | 3.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Limited space for extension. | 33/11 | Red
STANDLAKE |  | WITNEY & YARNTON | 4.93/13.1 | 51.718710 | -1.437575 | 6.50 | 0.00 | 0.48 | 6.00 | 2.00 | 3.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to Primary transformers limitations under FCO. | 33/11 | Red
WINDRUSH PARK |  | WITNEY & YARNTON | 8.46/16.0 | 51.785348 | -1.517554 | 30.00 | 0.00 | 3.59 | 13.25 | 0.03 | 3.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Upstream Voltage & thermal constraints. | 33/11 | Red
WITNEY TOWN |  | WITNEY & YARNTON | 11.62/13.1 | 51.784548 | -1.481697 | 24.00 | 0.00 | 4.99 | 22.07 | 0.00 | 3.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Red
WOODSTOCK |  | WITNEY & YARNTON | 7.81/13.1 | 51.854308 | -1.352402 | 15.00 | 0.00 | 2.26 | 8.29 | 0.51 | 3.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Limited space for extension. | 33/11 | Red
YARNTON |  | WITNEY & YARNTON | 11.33/25.0 | 51.805255 | -1.300936 | 40.00 | 0.00 | 4.78 | 23.40 | 4.98 | 3.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Red
BRENTFORD |  | EALING (D) | 11.07/25.0 | 51.491142 | -0.306493 | 31.80 | 0.00 | 7.48 | 29.19 | 0.00 | 39.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/11 | Green
DEAN GARDENS |  | EALING (D) | 4.15/13.1 | 51.510245 | -0.321781 | 6.00 | 0.00 | 0.84 | 4.45 | 0.00 | 6.00 | 50 | Unconstrained |  |  | Partially Constrained |  |  | No | No | Moderate proximity to Primary transformers limitations under FCO. | 22/11 | Amber
HARVARD LANE |  | EALING (D) | 8.82/13.1 | 51.488489 | -0.272598 | 26.60 | 0.00 | 8.78 | 24.16 | 1.60 | 33.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/11 | Green
BICESTER |  | BICESTER NORTH | 11.86/16.0 | 51.894397 | -1.152444 | 60.00 | 0.00 | 9.67 | 36.20 | 33.51 | 2.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to upstream thermal limitations. | 33/11 | Red
COTTISFORD |  | BICESTER NORTH | 2.29/13.1 | 51.975505 | -1.141306 | 2.50 | 0.00 | 0.25 | 2.30 | 10.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constrained due to upstream thermal limitations. | 33/11 | Red
UPPER HEYFORD |  | BICESTER NORTH | 8.1/13.1 | 51.927236 | -1.248245 | 15.00 | 0.00 | 1.18 | 4.50 | 7.39 | 2.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to upstream thermal limitations. Limited expansion space for CB connections. | 33/11 | Red
BINSTEAD |  | COWES & WOOTTON COMMON | 8.06/13.1 | 50.719586 | -1.202139 | 15.00 | 0.00 | 1.15 | 6.60 | 0.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 33/11 | Red
COWES POWER STATION |  | COWES & WOOTTON COMMON | 9.42/13.1 | 50.745665 | -1.285334 | 30.00 | 0.00 | 5.67 | 20.47 | 0.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 33/11 | Red
FRESHWATER |  | COWES & WOOTTON COMMON | 6.3/25.0 | 50.690462 | -1.515218 | 15.00 | 0.00 | 1.48 | 5.33 | 0.45 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 33/11 | Red
NEWPORT |  | COWES & WOOTTON COMMON | 11.22/13.1 | 50.699175 | -1.285744 | 38.00 | 0.00 | 6.74 | 31.95 | 0.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 33/11 | Red
RYDE |  | COWES & WOOTTON COMMON | 7.93/13.1 | 50.724321 | -1.158083 | 30.00 | 0.00 | 4.68 | 18.68 | 0.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 33/11 | Red
SANDOWN |  | COWES & WOOTTON COMMON | 7.71/13.1 | 50.661786 | -1.154589 | 15.00 | 0.00 | 2.84 | 12.19 | 1.98 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 33/11 | Red
SHALFLEET |  | COWES & WOOTTON COMMON | 7.36/25.0 | 50.695890 | -1.423415 | 15.00 | 0.00 | 1.02 | 6.21 | 0.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 33/11 | Red
SHANKLIN |  | COWES & WOOTTON COMMON | 7.17/13.1 | 50.634115 | -1.183648 | 30.00 | 0.00 | 2.94 | 12.37 | 0.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 33/11 | Red
VENTNOR |  | COWES & WOOTTON COMMON | 9.41/16.0 | 50.597503 | -1.208160 | 30.00 | 0.00 | 2.11 | 10.00 | 0.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 33/11 | Red
BUTTS ASH |  | LANGLEY | 11.21/25.0 | 50.849230 | -1.408317 | 23.00 | 0.00 | 3.95 | 16.79 | 11.50 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 33/11 | Red
LANGLEY |  | LANGLEY | 9.66/25 | 50.810127 | -1.360129 | 15.00 | 0.00 | 2.12 | 9.18 | 8.33 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 33/11 | Red
ALDERSHOT |  | ALDERSHOT | 17.18/25.0 | 51.231739 | -0.770767 | 19.50 | 0.00 | 2.58 | 13.25 | 2.40 | 19.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
FARNHAM |  | ALDERSHOT | 10.43/13.1 | 51.217392 | -0.791081 | 22.00 | 0.00 | 4.16 | 21.07 | 0.00 | 26.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
GODALMING |  | ALDERSHOT | 6.91/13.1 | 51.190192 | -0.616637 | 30.00 | 0.00 | 4.47 | 22.26 | 0.00 | 34.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
HINDHEAD |  | ALDERSHOT | 5.74/20.0 | 51.120665 | -0.734452 | 21.00 | 0.00 | 3.02 | 13.03 | 0.00 | 24.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
LABURNUM ROAD |  | ALDERSHOT | 12.25/25.0 | 51.246923 | -0.768672 | 36.30 | 0.00 | 6.36 | 25.49 | 0.00 | 42.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
MILFORD |  | ALDERSHOT | 6.43/20.0 | 51.178494 | -0.646744 | 24.00 | 0.00 | 2.77 | 11.72 | 0.18 | 26.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
NORMANDY |  | ALDERSHOT | 2.61/16.0 | 51.276543 | -0.665228 | 2.50 | 0.00 | 0.59 | 2.44 | 0.00 | 3.00 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations. | 33/11 | Red
TONGHAM |  | ALDERSHOT | 9.82/16.0 | 51.237677 | -0.736402 | 30.00 | 0.00 | 2.85 | 15.02 | 1.74 | 31.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ALRESFORD |  | ALTON & FERNHURST | 6.42/13.1 | 51.088903 | -1.149969 | 13.00 | 0.00 | 4.00 | 11.48 | 0.00 | 0.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ALTON LOCAL |  | ALTON & FERNHURST | 10.04/13.1 | 51.152594 | -0.961495 | 37.50 | 0.00 | 6.77 | 27.42 | 0.25 | 5.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
BORDON |  | ALTON & FERNHURST | 9.13/13.1 | 51.110205 | -0.826592 | 26.00 | 0.00 | 4.52 | 23.00 | 0.00 | 5.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
FIVE OAKS |  | ALTON & FERNHURST | 8.54/13.1 | 51.050234 | -0.422354 | 15.00 | 0.00 | 1.59 | 10.59 | 11.40 | 5.00 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations. | 33/11 | Red
HASLEMERE |  | ALTON & FERNHURST | 8.96/25.0 | 51.078214 | -0.725618 | 21.40 | 0.00 | 5.23 | 18.43 | 0.00 | 5.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
HASLINGBOURNE |  | ALTON & FERNHURST | 2.86/25.0 | 50.973479 | -0.602432 | 13.00 | 0.00 | 1.56 | 7.99 | 0.00 | 5.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
HERRIARD |  | ALTON & FERNHURST | 4.88/16.0 | 51.201855 | -1.046206 | 7.50 | 0.00 | 0.21 | 1.70 | 7.40 | 0.00 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations. | 33/11 | Red
LANGLEY COURT |  | ALTON & FERNHURST | 7.89/25.0 | 51.054929 | -0.847537 | 24.00 | 0.00 | 2.26 | 10.03 | 0.22 | 5.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
MIDHURST |  | ALTON & FERNHURST | 8.38/13.1 | 51.157971 | -1.558813 | 30.00 | 0.00 | 3.06 | 11.59 | 5.00 | 19.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
PETERSFIELD |  | ALTON & FERNHURST | 6.02/13.1 | 51.005398 | -0.944545 | 30.00 | 0.00 | 5.45 | 21.53 | 0.25 | 5.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
PLAISTOW |  | ALTON & FERNHURST | 3.39/20.0 | 51.056951 | -0.544984 | 4.85 | 0.00 | 0.99 | 4.59 | 0.32 | 10.00 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations. | 33/11 | Red
PRESTON CANDOVER |  | ALTON & FERNHURST | 7.28/25.0 | 51.166454 | -1.130667 | 15.00 | 0.00 | 1.06 | 4.75 | 20.00 | 0.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ASCOT |  | BRACKNELL MAIN | 7.91/25.0 | 51.411370 | -0.684025 | 30.00 | 0.00 | 4.89 | 15.50 | 0.00 | 34.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
BRACKNELL |  | BRACKNELL MAIN | 13.82/20.0 | 51.417297 | -0.764302 | 76.00 | 0.00 | 13.06 | 46.63 | 0.00 | 85.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
WARFIELD |  | BRACKNELL MAIN | 8.44/13.1 | 51.435836 | -0.750508 | 22.10 | 0.00 | 5.22 | 20.64 | 0.00 | 27.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
BAGSHOT |  | BRACKNELL RESERVE | 6.88/20.0 | 51.363417 | -0.692294 | 24.00 | 0.00 | 4.21 | 14.22 | 0.00 | 28.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
CHOBHAM |  | BRACKNELL RESERVE | 6.6/25.0 | 51.359564 | -0.605365 | 14.30 | 0.00 | 2.18 | 10.47 | 0.00 | 16.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
EASTHAMPSTEAD |  | BRACKNELL RESERVE | 8.97/25.0 | 51.397031 | -0.762778 | 30.00 | 0.00 | 4.63 | 19.00 | 0.00 | 34.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
MVEE |  | BRACKNELL RESERVE | 8.01/13.1 | 51.372094 | -1.105661 | 30.00 | 0.00 | 0.15 | 9.44 | 3.71 | 26.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
SUNNINGHILL |  | BRACKNELL RESERVE | 7.52/13.1 | 51.399416 | -0.652886 | 24.00 | 0.00 | 3.01 | 12.38 | 0.00 | 27.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/6.6 | Green
COURAGES |  | BURGHFIELD MAIN | 10.43/13.1 | 51.417354 | -0.977510 | 26.50 | 0.00 | 4.65 | 18.57 | 5.70 | 25.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
KENTWOOD HILL |  | BURGHFIELD MAIN | 10.71/16.0 | 51.461451 | -1.034822 | 21.90 | 0.00 | 4.12 | 19.37 | 0.00 | 26.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
WHITLEY WOOD |  | BURGHFIELD MAIN | 8.65/13.1 | 51.725716 | -1.971142 | 30.00 | 0.00 | 6.44 | 28.16 | 0.00 | 36.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
WILSON ROAD |  | BURGHFIELD MAIN | 11.35/25.0 | 51.454893 | -1.003297 | 27.60 | 0.00 | 3.84 | 15.71 | 0.00 | 31.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
GORING |  | BURGHFIELD RESERVE | 6.63/25.0 | 51.541712 | -1.131714 | 15.00 | 0.00 | 2.01 | 5.64 | 7.55 | 8.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
MORTIMER |  | BURGHFIELD RESERVE | 5.32/13.1 | 51.626634 | -1.976838 | 15.00 | 0.00 | 1.65 | 7.97 | 0.00 | 16.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
PADWORTH |  | BURGHFIELD RESERVE | 3.65/13.1 | 51.389187 | -1.106765 | 5.00 | 0.00 | 0.55 | 3.19 | 0.00 | 5.00 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations. | 33/11 | Red
PANGBOURNE |  | BURGHFIELD RESERVE | 8.51/25.0 | 51.481711 | -1.094878 | 30.00 | 0.00 | 1.89 | 9.11 | 0.00 | 27.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
SOUTHCOTE |  | BURGHFIELD RESERVE | 11.45/16.0 | 51.436147 | -1.019531 | 19.50 | 0.00 | 1.96 | 7.87 | 0.21 | 21.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
THEALE |  | BURGHFIELD RESERVE | 7.58/20.0 | 51.434399 | -1.069919 | 24.00 | 0.00 | 2.46 | 13.17 | 0.31 | 26.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
TRASH GREEN |  | BURGHFIELD RESERVE | 7.84/16.0 | 51.414795 | -1.047309 | 15.00 | 0.00 | 2.36 | 10.82 | 1.70 | 15.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
WOODCOTE |  | BURGHFIELD RESERVE | 3.67/16.0 | 51.530978 | -1.070836 | 5.00 | 0.00 | 1.01 | 3.94 | 0.00 | 6.00 | 50 | Unconstrained |  |  | Partially Constrained |  |  | Yes | Yes | Moderate proximity to Primary transformers limitations. | 33/11 | Amber
CAMBERLEY |  | CAMBERLEY MAIN | 13.67/25.0 | 51.327665 | -0.759335 | 80.00 | 0.00 | 9.49 | 27.10 | 0.00 | 85.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
CROWTHORNE |  | CAMBERLEY MAIN | 10.96/25.0 | 51.372204 | -0.787727 | 30.00 | 0.00 | 4.89 | 22.54 | 0.00 | 34.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
KINGS RIDE |  | CAMBERLEY MAIN | 10.43/13.1 | 51.345936 | -0.744052 | 24.00 | 0.00 | 3.39 | 13.57 | 0.00 | 27.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
SANDHURST |  | CAMBERLEY MAIN | 7.22/13.1 | 51.341324 | -0.801607 | 30.00 | 0.00 | 4.99 | 21.00 | 0.20 | 29.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
COVE |  | CAMBERLEY RESERVE | 7.61/13.1 | 51.296279 | -0.776102 | 24.00 | 0.00 | 2.37 | 9.63 | 0.00 | 26.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
FARNBOROUGH |  | CAMBERLEY RESERVE | 7.18/13.1 | 51.277396 | -0.733879 | 30.00 | 0.00 | 4.25 | 16.53 | 0.00 | 34.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
FRIMLEY |  | CAMBERLEY RESERVE | 7.79/12.5 | 51.314178 | -0.742624 | 30.00 | 0.00 | 4.84 | 23.81 | 1.40 | 33.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
QUEENSMEAD |  | CAMBERLEY RESERVE | 7.82/13.1 | 51.293695 | -0.752792 | 13.00 | 0.00 | 1.96 | 8.35 | 0.00 | 14.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
COXMOOR WOOD |  | COXMOOR WOOD | 4.99/16.0 | 51.250827 | -0.879759 | 9.50 | 0.00 | 1.97 | 7.26 | 0.00 | 5.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
CROOKHAM |  | COXMOOR WOOD | 11.05/25.0 | 51.273545 | -0.830465 | 24.00 | 0.00 | 2.13 | 12.26 | 0.00 | 24.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
HAWLEY |  | COXMOOR WOOD | 3.77/13.1 | 51.311483 | -0.768236 | 23.00 | 0.00 | 2.41 | 12.17 | 0.00 | 25.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
HITCHES LANE |  | COXMOOR WOOD | 8.55/13.1 | 51.286443 | -0.861829 | 40.00 | 0.00 | 6.45 | 24.18 | 4.26 | 28.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
HOOK |  | COXMOOR WOOD | 8.61/25.0 | 51.278545 | -0.960235 | 30.00 | 0.00 | 3.90 | 22.08 | 0.00 | 28.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
WRECCLESHAM |  | COXMOOR WOOD | 7.64/25.0 | 51.191848 | -0.825808 | 30.00 | 0.00 | 2.61 | 13.84 | 20.00 | 12.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
BRAYWICK ROAD |  | MAIDENHEAD | 9.96/13.1 | 51.518229 | -0.719574 | 30.00 | 0.00 | 7.36 | 26.93 | 0.08 | 17.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
CORDWALLIS |  | MAIDENHEAD | 9.27/13.1 | 51.528577 | -0.728510 | 30.00 | 0.00 | 6.43 | 20.90 | 0.00 | 17.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | None known | 33/11 | Red
KNOWL HILL |  | MAIDENHEAD | 5.55/25.0 | 51.504676 | -0.807269 | 6.50 | 0.00 | 0.55 | 4.14 | 0.00 | 7.00 | 50 | Unconstrained |  |  | Partially Constrained |  |  | Yes | Yes | Moderate proximity to Primary transformers limitations. | 33/11 | Amber
MAIDENHEAD |  | MAIDENHEAD | 13/13.1 | 50.778333 | -2.580047 | 45.00 | 0.00 | 6.09 | 25.87 | 0.00 | 17.14 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
TEMPLE FARM |  | MAIDENHEAD | 2.72/25.0 | 51.547365 | -0.787549 | 4.00 | 0.00 | 0.56 | 3.14 | 0.00 | 4.00 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | Yes | None known | 33/11 | Red
PYESTOCK 33/11 |  | PYESTOCK | 10.2/20.0 | 51.283964 | -0.811416 | 24.00 | 0.00 | 0.87 | 6.37 | 0.00 | 0.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
HENLEY |  | READING | 7.94/25.0 | 51.535828 | -0.903489 | 30.00 | 0.00 | 4.00 | 16.68 | 0.00 | 34.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
KIDMORE END |  | READING | 3.7/25.0 | 51.498858 | -0.992255 | 14.20 | 0.00 | 2.00 | 8.11 | 0.00 | 16.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
LITTLE HUNGERFORD |  | READING | 14.40/17.5 | 51.441541 | -0.917258 | 42.00 | 0.00 | 7.38 | 26.32 | 4.08 | 35.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
NORTHUMBERLAND AVENUE |  | READING | 12.83/25.0 | 51.433853 | -0.962036 | 25.00 | 0.00 | 5.06 | 17.66 | 3.00 | 27.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
PINGEWOOD |  | READING | 6.1/25.0 | 51.458778 | -0.926984 | 14.30 | 0.00 | 1.40 | 9.72 | 0.00 | 15.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
READING |  | READING | 14.75/20.0 | 51.458778 | -0.926998 | 55.00 | 0.00 | 11.17 | 33.01 | 1.14 | 65.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
SILVER STREET |  | READING | 12.22/13.1 | 51.450074 | -0.965986 | 26.60 | 0.00 | 4.43 | 18.88 | 7.00 | 24.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Moderate proximity to fault rating. | 33/11 | Green
TWYFORD |  | READING | 6.67/13.1 | 51.481575 | -0.871668 | 15.00 | 0.00 | 2.57 | 11.49 | 0.10 | 17.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
CAVERSHAM |  | READING TOWN | 8.5/13.1 | 51.476183 | -0.969716 | 30.00 | 0.00 | 2.73 | 12.70 | 0.00 | 32.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
READING TOWN |  | READING TOWN | 8.40/13.1 | 51.461558 | -0.971283 | 60.00 | 0.00 | 8.78 | 37.91 | 0.50 | 68.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
THE MALL |  | READING TOWN | 9.61/13.1 | 51.454644 | -0.974518 | 26.50 | 0.00 | 4.53 | 19.56 | 0.15 | 30.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ELMS ROAD |  | WOKINGHAM | 10.11/25.0 | 51.410192 | -0.836185 | 30.00 | 0.00 | 4.42 | 23.55 | 0.00 | 34.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
PEACOCK FARM |  | WOKINGHAM | 7.36/25.0 | 51.384238 | -0.591006 | 15.00 | 0.00 | 1.23 | 5.48 | 0.00 | 16.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
WOKINGHAM |  | WOKINGHAM | 7.98/25.0 | 51.402441 | -0.857241 | 30.00 | 0.00 | 2.19 | 9.39 | 0.00 | 32.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
CHALVEY |  | CHALVEY | 13.71/25.0 | 51.504468 | -0.607242 | 76.00 | 6.00 | 11.49 | 38.62 | 8.80 | 49.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
PETERSFIELD AVENUE |  | CHALVEY | 18.63/25.0 | 51.513300 | -0.587849 | 42.00 | 0.00 | 7.96 | 32.29 | 3.94 | 46.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
CLARENCE ROAD |  | CIPPENHAM | 12.21/25.0 | 51.480638 | -0.623853 | 45.00 | 0.00 | 8.84 | 32.38 | 0.00 | 53.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
BEACONSFIELD (MIDDLE B/B) |  | DENHAM | 9.17/25.0 | 51.611847 | -0.648485 | 12.90 | 0.00 | 3.22 | 11.36 | 0.00 | 16.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/6.6 | Green
COKES LANE |  | DENHAM | 10.94/13.1 | 51.667516 | -0.565852 | 16.20 | 0.00 | 1.27 | 7.04 | 0.00 | 17.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/6.6 | Green
DENHAM AVENUE |  | DENHAM | 12.50/13.1 | 51.568912 | -0.504026 | 13.00 | 0.00 | 3.40 | 11.07 | 0.00 | 16.00 | 50 | Unconstrained |  |  | Partially Constrained |  |  | No | No | Moderate proximity to fault rating | 22/6.6 | Amber
GERRARDS CROSS |  | DENHAM | 13.10/25.0 | 51.582007 | -0.558875 | 15.20 | 0.00 | 3.63 | 14.01 | 0.00 | 18.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/6.6 | Green
GRASSINGHAM ROAD |  | DENHAM | 12.41/13.1 | 51.609023 | -0.554843 | 26.00 | 0.00 | 4.55 | 13.24 | 0.00 | 30.00 | 50 | Unconstrained |  |  | Constrained |  |  | No | No | Moderate proximity to fault rating. | 22/6.6 | Amber
HAREFIELD |  | DENHAM | 9.34/25.0 | 51.610213 | -0.499203 | 10.00 | 0.00 | 1.26 | 5.10 | 0.00 | 11.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/6.6 | Green
BATH ROAD WEST |  | LONGFORD | 13.57/13.1 | 51.480268 | -0.477550 | 25.10 | 0.00 | 6.26 | 14.42 | 0.00 | 31.00 | 50 | Unconstrained |  |  | Constrained |  |  | No | No | Proximity to fault level | 33/11 | Red
POYLE |  | LONGFORD | 10.99/25.0 | 51.469295 | -0.512326 | 25.70 | 0.00 | 6.49 | 19.91 | 0.00 | 32.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
FARNHAM ROYAL |  | SLOUGH | 13.25/25.0 | 51.536555 | -0.622744 | 48.00 | 0.00 | 7.08 | 26.84 | 12.00 | 43.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
TAPLOW |  | SLOUGH | 9.82/25.0 | 51.522734 | -0.679809 | 23.00 | 0.00 | 3.87 | 17.62 | 0.00 | 26.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
BEACONSFIELD (END B/B) |  | UPTON | 3.39/25.0 | 51.611847 | -0.648485 | 6.50 | 0.00 | 1.00 | 4.44 | 0.00 | 6.00 | 50 | Unconstrained |  |  | Partially Constrained |  |  | No | No | Moderate proximity to Primary transformers limitations under FCO. | 22/6.6 | Amber
SUTTON LANE |  | UPTON | 8.35/25.0 | 51.490276 | -0.534718 | 24.00 | 0.00 | 1.62 | 8.82 | 8.80 | 17.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/11 | Green
UPTON |  | UPTON | 10.40/13.1 | 51.504952 | -0.548512 | 26.00 | 0.00 | 5.57 | 22.25 | 0.40 | 31.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/11 | Green
CHURCH ROAD |  | EAST BEDFONT A | 7.41/13.1 | 51.434274 | -0.464563 | 14.00 | 0.00 | 1.86 | 12.76 | 0.00 | 15.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/11 | Green
FELTHAM |  | EAST BEDFONT A | 12.05/13.1 | 51.443393 | -0.409275 | 27.90 | 0.00 | 3.88 | 11.88 | 0.00 | 31.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/6.6 | Green
HOPE AND ANCHOR |  | EAST BEDFONT A | 7.63/13.1 | 51.436156 | -0.379889 | 7.00 | 26.00 | 0.49 | 2.52 | 0.00 | 7.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/6.6 | Green
NORTH FELTHAM |  | EAST BEDFONT A | 9.86/25.0 | 51.462108 | -0.403442 | 28.70 | 0.00 | 6.61 | 22.73 | 0.00 | 35.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/11 | Green
SUNGARD |  | EAST BEDFONT A | 6.97/25.0 | 51.468626 | -0.398723 | 23.00 | 0.00 | 6.46 | 8.08 | 0.00 | 29.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/11 | Green
CAUSEWAY |  | STAINES | 13.94/25.0 | 51.434722 | -0.523232 | 43.20 | 0.00 | 6.33 | 23.10 | 6.10 | 43.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
EGHAM |  | STAINES | 10.31/20.0 | 51.432454 | -0.548221 | 28.00 | 0.00 | 7.90 | 25.75 | 0.00 | 35.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
SIDNEY ROAD |  | STAINES | 9.39/13.1 | 51.435106 | -0.503797 | 21.40 | 0.00 | 3.34 | 13.65 | 1.30 | 23.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
STANWELL |  | STAINES | 9.24/13.1 | 51.443371 | -0.475324 | 19.60 | 0.00 | 3.22 | 9.11 | 0.00 | 22.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
SUNBURY CROSS |  | STAINES | 10/13.1 | 51.418431 | -0.418627 | 52.70 | 0.00 | 11.93 | 38.42 | 15.40 | 49.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
ARGYLE ROAD |  | CHICHESTER & HUNSTON | 10.63/13.1 | 50.784349 | -0.678936 | 30.00 | 0.00 | 3.72 | 18.81 | 0.00 | 9.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
ASHLING ROAD |  | CHICHESTER & HUNSTON | 10.93/13.1 | 50.854113 | -0.807130 | 26.00 | 0.00 | 5.82 | 22.59 | 1.90 | 9.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | Rhere is no reverse power capacity at the BSB and new generations will requier new BSP Transformer | 33/11 | Amber
BILLINGSHURST |  | CHICHESTER & HUNSTON | 2.91/20.0 | 51.025967 | -0.457045 | 10.00 | 0.00 | 1.45 | 7.75 | 0.00 | 9.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | Rhere is no reverse power capacity at the BSB and new generations will requier new BSP Transformer | 33/11 | Amber
BILSHAM |  | CHICHESTER & HUNSTON | 10.88/13.1 | 50.805449 | -0.619287 | 30.00 | 0.00 | 3.67 | 15.63 | 34.97 | 0.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | Rhere is no reverse power capacity at the BSB and new generations will requier new BSP Transformer | 33/11 | Amber
BIRDHAM |  | CHICHESTER & HUNSTON | 7.46/13.1 | 50.788517 | -0.838561 | 10.00 | 0.00 | 2.98 | 11.26 | 0.00 | 9.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | Rhere is no reverse power capacity at the BSB and new generations will requier new BSP Transformer | 33/11 | Amber
CHICHESTER |  | CHICHESTER & HUNSTON | 13.12/25.0 | 50.858912 | -0.690243 | 23.00 | 0.00 | 3.42 | 16.07 | 16.35 | 9.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | Rhere is no reverse power capacity at the BSB and new generations will requier new BSP Transformer | 33/11 | Amber
HUNSTON |  | CHICHESTER & HUNSTON | 12.08/25.0 | 50.816718 | -0.767115 | 30.00 | 0.00 | 5.50 | 28.32 | 18.00 | 5.36 | 50 | Unconstrained |  |  | Partially Constrained | AVC Upgrade | 01/09/21 | No | Yes | Rhere is no reverse power capacity at the BSB and new generations will requier new BSP Transformer | 33/11 | Amber
MARKET |  | CHICHESTER & HUNSTON | 10.71/13.1 | 50.846463 | -1.894513 | 20.00 | 0.00 | 3.20 | 15.02 | 0.00 | 9.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | Rhere is no reverse power capacity at the BSB and new generations will requier new BSP Transformer | 33/11 | Amber
ROSE GREEN |  | CHICHESTER & HUNSTON | 11.07/13.1 | 50.786752 | -0.725187 | 20.00 | 0.00 | 2.00 | 15.43 | 8.05 | 9.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | Rhere is no reverse power capacity at the BSB and new generations will requier new BSP Transformer | 33/11 | Amber
SELSEY |  | CHICHESTER & HUNSTON | 6.93/20.0 | 50.741602 | -0.787088 | 11.90 | 0.00 | 3.70 | 9.52 | 0.00 | 9.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | Rhere is no reverse power capacity at the BSB and new generations will requier new BSP Transformer | 33/11 | Amber
SOUTH BERSTED |  | CHICHESTER & HUNSTON | 11.42/16.0 | 50.797971 | -0.666845 | 20.00 | 0.00 | 4.20 | 19.63 | 0.31 | 9.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | Rhere is no reverse power capacity at the BSB and new generations will requier new BSP Transformer | 33/11 | Amber
BROCKHURST |  | FAREHAM MAIN | 9.47/13.1 | 50.816034 | -1.157344 | 30.00 | 0.00 | 7.46 | 21.89 | 0.00 | 26.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | Partialy constraint due to limited reverse power capacity | 33/11 | Amber
HOEFORD |  | FAREHAM MAIN | 10.07/13.1 | 50.836514 | -1.179413 | 19.50 | 0.00 | 4.52 | 15.05 | 0.50 | 23.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | Partialy constraint due to limited reverse power capacity | 33/11 | Amber
NORTH FAREHAM |  | FAREHAM MAIN | 7.5/13.1 | 50.863987 | -1.198825 | 15.20 | 0.00 | 2.39 | 11.96 | 0.00 | 17.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | Partialy constraint due to limited reverse power capacity | 33/11 | Amber
PLESSEY TITCHFIELD |  | FAREHAM MAIN | 8.07/12.5 | 50.833777 | -1.199626 | 30.00 | 0.00 | 4.13 | 12.82 | 0.00 | 16.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | Partialy constraint due to limited reverse power capacity | 33/11 | Amber
TITCHFIELD |  | FAREHAM MAIN | 10.01/13.1 | 50.830314 | -1.233054 | 15.00 | 0.00 | 2.17 | 9.57 | 0.32 | 17.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | Partialy constraint due to limited reverse power capacity | 33/11 | Amber
WEST END |  | FAREHAM MAIN | 11.7/13.1 | 50.852038 | -1.187523 | 30.00 | 0.00 | 3.46 | 13.69 | 0.00 | 26.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | Partialy constraint due to limited reverse power capacity | 33/11 | Amber
LEE-ON-SOLENT |  | FAREHAM RESERVE | 7.74/13.1 | 50.799304 | -1.195106 | 24.00 | 0.00 | 3.15 | 12.69 | 0.00 | 24.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | Partialy constraint due to limited reverse power capacity | 33/11 | Amber
ROWNER PARK |  | FAREHAM RESERVE | 8.92/13.1 | 50.803220 | -1.176449 | 30.00 | 0.00 | 2.38 | 8.29 | 0.00 | 24.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | Partialy constraint due to limited reverse power capacity | 33/11 | Amber
ZETLAND ROAD |  | FAREHAM RESERVE | 10.17/13.1 | 50.796948 | -1.142079 | 26.00 | 0.00 | 6.54 | 18.86 | 0.00 | 24.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | Partialy constraint due to limited reverse power capacity | 33/11 | Amber
BROCKHAMPTON |  | HAVANT | 12.26/25 | 50.847657 | -0.994415 | 30.00 | 0.00 | 5.35 | 15.20 | 16.62 | 18.00 | 50 | Unconstrained |  |  | Unconstrained | Switchgear -E reinforcement due to make issue (FL results include new rating). | 01/03/22 | No | Yes |  | 33/11 | Green
EMSWORTH |  | HAVANT | 8.14/25.0 | 50.846878 | -0.937926 | 13.00 | 0.00 | 2.37 | 10.03 | 0.87 | 14.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
GABLE HEAD |  | HAVANT | 8.4/13.1 | 50.794354 | -0.976547 | 30.00 | 0.00 | 2.96 | 12.85 | 0.24 | 32.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
HORNDEAN |  | HAVANT | 4.95/13.1 | 50.910675 | -1.002446 | 30.00 | 0.00 | 2.37 | 20.70 | 8.00 | 24.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
LEIGH PARK |  | HAVANT | 13.0/25 | 50.865483 | -0.976127 | 30.50 | 0.00 | 4.58 | 21.17 | 3.74 | 31.00 | 50 | Unconstrained |  |  | Unconstrained | Switchgear -E reinforcement (Completed. FL results include new rating). |  | No | Yes | Proximity to fault rating | 33/11 | Green
MEYRICK ROAD |  | HAVANT | 8.45/25.0 | 51.374742 | -2.143935 | 25.40 | 0.00 | 4.34 | 17.58 | 0.00 | 29.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
BRANDON ROAD |  | PORTSMOUTH | 8.55/25.0 | 50.783820 | -1.083167 | 26.00 | 0.00 | 4.51 | 17.81 | 0.00 | 30.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
EASTNEY |  | PORTSMOUTH | 8.87/13.1 | 50.789008 | -1.046037 | 20.00 | 0.00 | 1.47 | 7.57 | 0.00 | 21.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
FRATTON PARK |  | PORTSMOUTH | 11.20/13.1 | 50.797238 | -1.062897 | 34.00 | 0.00 | 6.55 | 26.26 | 0.00 | 40.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
GREETHAM STREET |  | PORTSMOUTH | 9.05/13.1 | 50.797616 | -1.087863 | 30.00 | 0.00 | 3.93 | 14.85 | 0.20 | 33.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
PORTSMOUTH |  | PORTSMOUTH | 11.35/25.0 | 50.793272 | -1.101781 | 40.00 | 0.00 | 4.10 | 13.78 | 1.25 | 23.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
COLLEGE PARK |  | WYMERING & FORT WIDLEY | 9.05/13.1 | 50.819744 | -1.065854 | 13.00 | 0.00 | 2.81 | 11.43 | 0.00 | 15.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
FARLINGTON |  | WYMERING & FORT WIDLEY | 11.23/13.1 | 50.838989 | -1.043741 | 26.00 | 0.00 | 2.83 | 10.88 | 0.00 | 25.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
GAMBLE ROAD |  | WYMERING & FORT WIDLEY | 9.34/25.0 | 50.812862 | -1.082598 | 30.00 | 0.00 | 5.41 | 19.96 | 0.80 | 25.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
HILSEA |  | WYMERING & FORT WIDLEY | 8.56/13.1 | 50.829669 | -1.058840 | 30.00 | 0.00 | 3.15 | 15.70 | 0.33 | 25.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
PORTCHESTER |  | WYMERING & FORT WIDLEY | 11.14/13.1 | 50.847142 | -1.119994 | 19.50 | 0.00 | 2.85 | 14.75 | 3.50 | 18.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
PURBROOK |  | WYMERING & FORT WIDLEY | 8.22/13.1 | 50.866095 | -1.048444 | 13.00 | 0.00 | 2.83 | 8.23 | 0.00 | 15.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
WATERLOOVILLE |  | WYMERING & FORT WIDLEY | 10.61/13.1 | 50.878931 | -1.034537 | 45.00 | 0.00 | 4.98 | 20.79 | 0.05 | 25.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
WYMERING |  | WYMERING & FORT WIDLEY | 9.58/20.0 | 50.844856 | -1.078875 | 60.00 | 0.00 | 15.26 | 42.14 | 4.14 | 25.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
HINCHESLEA |  | ARNEWOOD | 7.06/13.1 | 50.802762 | -1.605588 | 15.00 | 0.00 | 1.91 | 6.95 | 0.00 | 16.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
LYMINGTON |  | ARNEWOOD | 9.28/13.1 | 50.770551 | -1.551120 | 30.00 | 0.00 | 4.79 | 17.54 | 2.17 | 0.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
MILFORD-ON-SEA |  | ARNEWOOD | 7.28/25.0 | 50.738808 | -1.600882 | 13.00 | 0.00 | 1.65 | 8.73 | 0.00 | 14.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | No spare bay. | 33/11 | Red
NEW MILTON |  | ARNEWOOD | 9.26/13.1 | 50.753691 | -1.673194 | 30.00 | 0.00 | 4.56 | 20.70 | 1.75 | 32.00 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | Yes | No spare bay. | 33/11 | Red
ALDERNEY |  | BOURNEMOUTH | 13.05/13.1 | 50.755481 | -1.938990 | 24.00 | 0.00 | 4.47 | 17.94 | 8.90 | 19.00 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | Yes | Proximity to fault rating. | 33/11 | Red
BOURNE VALLEY |  | BOURNEMOUTH | 8.96/13.1 | 50.731517 | -1.912581 | 30.00 | 0.00 | 5.15 | 23.71 | 0.00 | 35.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
CENTRAL |  | BOURNEMOUTH | 10.22/13.1 | 50.727080 | -1.854728 | 30.00 | 0.00 | 7.12 | 28.47 | 5.40 | 31.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Constrained due to upstream thermal limitations. | 33/11 | Green
ELECTRIC HOUSE |  | BOURNEMOUTH | 11.84/13.1 | 50.721711 | -1.878119 | 26.00 | 0.00 | 5.89 | 21.53 | 0.25 | 31.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
PARKSTONE NORTH |  | BOURNEMOUTH | 9.58/13.1 | 50.730309 | -1.954608 | 29.80 | 0.00 | 5.97 | 24.89 | 0.00 | 35.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
PARKSTONE SOUTH |  | BOURNEMOUTH | 11.38/25.0 | 50.707817 | -1.933386 | 30.00 | 0.00 | 2.58 | 9.24 | 0.00 | 32.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
WESTBOURNE |  | BOURNEMOUTH | 9.54/13.1 | 50.723074 | -1.892282 | 30.00 | 0.00 | 4.52 | 16.17 | 0.00 | 34.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
BOSCOMBE EAST |  | CHRISTCHURCH | 10.11/13.1 | 50.732002 | -1.836292 | 26.50 | 0.00 | 4.56 | 14.59 | 0.00 | 31.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
CHRISTCHURCH |  | CHRISTCHURCH | 8.87/20.0 | 50.738651 | -1.778875 | 39.00 | 0.00 | 5.61 | 22.30 | 0.00 | 30.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
SOMERFORD |  | CHRISTCHURCH | 11.62/13.1 | 50.742173 | -1.742011 | 26.00 | 0.00 | 4.94 | 18.78 | 1.00 | 20.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
SOUTHBOURNE |  | CHRISTCHURCH | 11.74/25.0 | 50.727914 | -1.809387 | 19.50 | 0.00 | 2.71 | 11.83 | 0.00 | 20.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
BLANDFORD |  | LYTCHETT | 6.22/20.0 | 50.848909 | -2.160461 | 30.70 | 0.00 | 4.78 | 16.56 | 0.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Green
CORFE MULLEN |  | LYTCHETT | 8.55/13.1 | 50.765387 | -2.019799 | 30.00 | 0.00 | 1.36 | 16.23 | 1.15 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
CREEKMOOR |  | LYTCHETT | 10.94/13.1 | 50.746504 | -1.992861 | 26.00 | 0.00 | 3.51 | 14.64 | 1.02 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Green
HOLES BAY |  | LYTCHETT | 9.86/25.0 | 50.727170 | -1.991164 | 30.00 | 0.00 | 4.17 | 19.86 | 7.87 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Green
WINTERBORNE KINGSTON |  | LYTCHETT | 6.1/13.1 | 50.747525 | -2.032591 | 9.80 | 0.00 | 1.61 | 6.38 | 0.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
FERNDOWN |  | MANNINGTON | 11.38/13.0 | 50.805819 | -1.906993 | 45.00 | 0.00 | 6.09 | 23.64 | 0.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Green
FORDINGBRIDGE |  | MANNINGTON | 6.41/13.1 | 50.939044 | -1.800984 | 15.00 | 0.00 | 1.53 | 6.52 | 0.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | No spare bay.BSP Transformer rating under N-1 | 33/11 | Red
HINTON MARTELL |  | MANNINGTON | 2.64/7.9 | 50.853785 | -1.991283 | 4.00 | 0.00 | 0.33 | 1.56 | 0.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations under FCO. | 33/11 | Red
MANNINGTON |  | MANNINGTON | 8.17/13.1 | 51.564575 | -1.782255 | 15.00 | 0.00 | 0.88 | 7.27 | 0.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Green
MILL LANE |  | MANNINGTON | 8.88/13.1 | 50.738808 | -1.600882 | 22.90 | 0.00 | 5.35 | 18.77 | 8.60 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | None known | 33/11 | Green
NEW STREET |  | MANNINGTON | 4.11/25.0 | 50.841628 | -1.785207 | 5.00 | 0.00 | 0.41 | 1.79 | 0.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations under FCO. | 33/11 | Red
ROCKBOURNE |  | MANNINGTON | 1.39/16.0 | 50.959601 | -1.835922 | 2.00 | 0.00 | 0.27 | 1.64 | 0.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations under FCO. | 33/11 | Red
VERWOOD |  | MANNINGTON | 6.79/13.1 | 50.891324 | -1.891611 | 13.00 | 0.00 | 2.06 | 10.08 | 5.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | 33kV upstream restrictions. No spare bay. | 33/11 | Red
WIMBORNE |  | MANNINGTON | 8.46/13.1 | 50.798658 | -1.972988 | 19.50 | 0.00 | 3.84 | 18.42 | 0.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
WIMBORNE ST GILES |  | MANNINGTON | 2.85/12.0 | 50.913668 | -1.958556 | 1.50 | 0.00 | 0.22 | 1.07 | 0.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations under FCO. | 33/11 | Red
HAMWORTHY |  | POOLE PS (HAMWORTHY) | 8.4/13.1 | 50.716496 | -1.999834 | 22.90 | 0.00 | 5.23 | 18.58 | 0.00 | 0.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
POOLE (HILL STREET) |  | POOLE PS (HAMWORTHY) | 12.6/13.1 | 51.411032 | -0.782574 | 23.00 | 0.00 | 4.80 | 15.02 | 3.40 | 0.00 | 50 | Unconstrained |  |  | Constrained |  |  | No | Yes | Proximity to fault rating | 33/11 | Red
EAST HOWE |  | REDHILL | 10.33/13.1 | 50.756807 | -1.904964 | 30.00 | 0.00 | 4.66 | 21.14 | 0.00 | 20.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Green
REDHILL |  | REDHILL | 8.5/25.0 | 50.764985 | -1.879694 | 39.00 | 0.00 | 3.35 | 21.60 | 8.71 | 20.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
WINTON |  | REDHILL | 12.65/13.1 | 50.747780 | -1.868838 | 26.00 | 0.00 | 5.86 | 19.81 | 5.06 | 20.00 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | Yes | Proximity to fault rating | 33/11 | Amber
BEMERTON |  | SALISBURY | 8.42/20.0 | 51.079826 | -1.835356 | 30.00 | 0.00 | 3.76 | 13.94 | 0.00 | 0.00 | 50 | Constrained |  |  | Unconstrained | Bemerton-C switchgear reinforcement | 01/06/21 | Yes | Yes | Constrained due to upstream thermal limitations. | 33/11 | Green
HOMINGTON |  | SALISBURY | 3.97/25.0 | 51.024252 | -1.833841 | 15.00 | 0.00 | 1.49 | 4.92 | 0.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations under FCO. | 33/11 | Green
NETHERHAMPTON |  | SALISBURY | 8.1/13.1 | 51.060925 | -1.823293 | 13.00 | 0.00 | 0.96 | 4.09 | 0.00 | 0.00 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to upstream thermal limitations. | 33/11 | Green
PETERSFINGER |  | SALISBURY | 6.61/13.1 | 51.065346 | -1.779037 | 14.00 | 0.00 | 2.40 | 11.77 | 0.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Constrained due to upstream thermal limitations. | 33/11 | Red
REDLYNCH |  | SALISBURY | 3.90/13.1 | 50.984042 | -1.729420 | 9.00 | 0.00 | 1.45 | 7.26 | 7.60 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations under FCO. | 33/11 | Red
SALISBURY CENTRAL |  | SALISBURY | 13.4/17.5 | 51.073186 | -1.798625 | 40.00 | 0.00 | 7.64 | 26.06 | 0.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Constrained due to upstream thermal limitations. | 33/11 | Red
STAPLEFORD |  | SALISBURY | 6.3/13.1 | 51.132685 | -1.903339 | 13.00 | 0.00 | 1.49 | 6.05 | 0.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Constrained due to upstream thermal limitations. | 33/11 | Red
TEFFONT |  | SALISBURY | 3.05/13.1 | 51.077873 | -2.002804 | 4.50 | 0.00 | 1.83 | 3.86 | 0.00 | 0.00 | 50 | Constrained |  |  | Partially Constrained |  |  | Yes | Yes | Moderate proximity to Primary transformers limitations under FCO. | 33/11 | Red
BOURTON |  | SHAFTESBURY | 6.61/20.0 | 51.076077 | -2.323259 | 13.00 | 0.00 | 2.04 | 10.15 | 1.50 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
GILLINGHAM |  | SHAFTESBURY | 6.53/25.0 | 51.030912 | -2.283985 | 30.00 | 0.00 | 1.36 | 5.57 | 0.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Green
GUSSAGE ST MICHAEL |  | SHAFTESBURY | 2.42/16.0 | 50.902199 | -2.020853 | 3.00 | 0.00 | 0.23 | 1.27 | 0.00 | 3.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations under FCO. | 33/11 | Red
MINCHINGTON |  | SHAFTESBURY | 2.53/12.0 | 51.624605 | -1.279113 | 5.00 | 0.00 | 0.43 | 2.96 | 0.00 | 0.00 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
SHAFTESBURY |  | SHAFTESBURY | 9.5/16.0 | 51.013311 | -2.208897 | 13.00 | 0.00 | 2.83 | 12.05 | 0.32 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
SHROTON |  | SHAFTESBURY | 6.83/25.0 | 50.921760 | -2.209226 | 24.00 | 0.00 | 2.46 | 14.73 | 6.60 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
TARRANT RUSHTON |  | SHAFTESBURY | 4.55/25.0 | 50.865179 | -2.079522 | 4.00 | 0.00 | 1.07 | 3.53 | 0.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations under FCO. | 33/11 | Red
TISBURY |  | SHAFTESBURY | 4.95/25.0 | 51.061648 | -2.095556 | 9.12 | 0.00 | 1.11 | 5.26 | 0.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
WEST STOUR |  | SHAFTESBURY | 6.4/13.1 | 50.997676 | -2.319151 | 9.80 | 0.00 | 0.95 | 4.85 | 0.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
WINCANTON |  | SHAFTESBURY | 6.62/25.0 | 51.048647 | -2.410231 | 15.00 | 0.00 | 2.26 | 8.29 | 5.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
BOVINGTON |  | WAREHAM | 6.97/13.1 | 50.690073 | -2.229994 | 9.80 | 0.00 | 1.15 | 4.58 | 5.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
BUSHEY |  | WAREHAM | 2.49/13.1 | 50.651500 | -2.034150 | 3.50 | 0.00 | 0.48 | 1.83 | 0.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to upstream thermal limitations. | 33/11 | Red
SWANAGE |  | WAREHAM | 5.29/25.0 | 50.613409 | -1.973800 | 13.00 | 0.00 | 2.69 | 9.32 | 0.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to upstream thermal limitations. | 33/11 | Red
WAREHAM TOWN |  | WAREHAM | 7.54/13.1 | 50.687096 | -2.114609 | 13.90 | 0.00 | 2.85 | 11.35 | 0.10 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to upstream thermal limitations. | 33/11 | Red
ANDOVER |  | ANDOVER | 8.450/25.0 | 51.217494 | -1.495475 | 30.00 | 0.00 | 1.77 | 9.96 | 0.00 | 0.60 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | BSP &132kV circuit therml constraints | 33/11 | Red
ANDOVER EAST |  | ANDOVER | 8.33/13.1 | 51.215983 | -1.455174 | 30.00 | 0.00 | 6.62 | 21.86 | 0.00 | 0.60 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | BSP &132kV circuit therml constraints | 33/11 | Red
ANDOVER TOWN |  | ANDOVER | 8.61/16.0 | 51.204411 | -1.481075 | 13.00 | 0.00 | 2.11 | 9.16 | 0.00 | 15.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | BSP &132kV circuit therml constraints | 33/11 | Red
BARTON STACEY |  | ANDOVER | 4.6/7.9 | 51.182434 | -1.398341 | 7.80 | 0.00 | 1.53 | 7.25 | 0.00 | 0.60 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Potential votlage issue, BSP &132kV circuit therml constraints | 33/11 | Red
HURSTBOURNE TARRANT |  | ANDOVER | 4.2/25.0 | 51.269843 | -1.435903 | 6.50 | 0.00 | 1.23 | 5.57 | 0.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Wide constraints on 33kV, 132kV systems and BSP capacity. | 33/11 | Red
MIDDLE WALLOP |  | ANDOVER | 4.37/13.1 | 51.159775 | -1.558081 | 7.00 | 0.00 | 0.80 | 6.08 | 4.80 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Wide constraints on 33kV, 132kV systems and BSP capacity. | 33/11 | Red
PORTWAY |  | ANDOVER | 9.63/13.1 | 51.212626 | -1.509616 | 26.00 | 0.00 | 1.96 | 19.30 | 8.06 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constrained by 132kV system and BSP capacity. | 33/11 | Red
THRUXTON |  | ANDOVER | 4.86/13.1 | 51.209499 | -1.584518 | 6.50 | 0.00 | 1.09 | 4.98 | 0.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Wide constraints on 33kV, 132kV systems and BSP capacity. | 33/11 | Red
WHITCHURCH |  | ANDOVER | 4.33/13.1 | 51.236082 | -1.341779 | 6.50 | 0.00 | 0.80 | 4.10 | 0.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Wide constraints on 33kV, 132kV systems and BSP capacity. | 33/11 | Red
ALDERTON |  | CHIPPENHAM | 3.23/13.1 | 51.555214 | -2.222075 | 3.90 | 0.00 | 0.52 | 3.04 | 0.00 | 0.15 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to upstream thermal limitations. | 33/11 | Red
CALNE |  | CHIPPENHAM | 11.56/13.1 | 51.451304 | -1.993907 | 21.00 | 0.00 | 3.30 | 17.33 | 12.50 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to upstream thermal limitations. | 33/11 | Red
COCKLEBURY |  | CHIPPENHAM | 12.1/13.1 | 51.463750 | -2.110215 | 35.50 | 0.00 | 4.60 | 17.24 | 0.00 | 1.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to upstream thermal limitations. | 33/11 | Red
LYNEHAM |  | CHIPPENHAM | 7.21/13.1 | 51.523055 | -2.011338 | 13.70 | 0.00 | 2.58 | 11.30 | 2.75 | 1.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to upstream thermal limitations. | 33/11 | Red
MALMESBURY |  | CHIPPENHAM | 7.1/13.1 | 51.511395 | -0.752910 | 13.00 | 0.00 | 3.90 | 11.40 | 0.50 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to upstream thermal limitations. | 33/11 | Red
ROWDEN |  | CHIPPENHAM | 8.93/13.1 | 51.452576 | -2.133790 | 23.00 | 0.00 | 4.14 | 20.55 | 0.00 | 1.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to upstream thermal limitations. | 33/11 | Red
SUTTON BENGER |  | CHIPPENHAM | 6.81/13.1 | 51.519689 | -2.096803 | 9.75 | 0.00 | 0.72 | 9.37 | 0.91 | 0.00 | 50 | Constrained |  |  | Constrained | Transformer upgrade | 01/03/20 | No | No | Constrained due to upstream thermal limitations. | 33/11 | Red
TETBURY |  | CHIPPENHAM | 6.22/13.1 | 51.639667 | -2.149947 | 9.80 | 0.00 | 1.68 | 7.00 | 0.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to Primary transformers limitations under FCO. | 33/11 | Red
YATTON KEYNELL |  | CHIPPENHAM | 3.0/13.1 | 51.480111 | -2.184270 | 5.00 | 0.00 | 1.03 | 6.10 | 0.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to upstream thermal limitations. | 33/11 | Red
BRUTON |  | FROME | 2.77/25.0 | 51.115073 | -2.442107 | 8.00 | 0.00 | 1.16 | 5.90 | 0.83 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constrained by BSP thermal capacity. | 33/11 | Red
CODFORD |  | FROME | 3.66/25.0 | 51.155360 | -2.039056 | 6.50 | 0.00 | 1.55 | 3.45 | 2.00 | 0.00 | 50 | Constrained |  |  | Partially Constrained |  |  | Yes | No | Constrained due to upstream thermal and voltage limitations. | 33/11 | Red
CROCKERTON |  | FROME | 7.25/13.1 | 51.188880 | -2.177381 | 17.00 | 0.00 | 2.59 | 12.11 | 1.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | BSP thermal capacity constraint. | 33/11 | Red
FROME |  | FROME | 6.80/13.1 | 51.230966 | -2.305868 | 46.00 | 2.53 | 7.53 | 28.23 | 2.72 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constrained by BSP thermal capacity. | 33/11 | Red
HAWKERIDGE |  | FROME | 13.41/25.0 | 51.276153 | -2.195695 | 15.00 | 18.30 | 3.56 | 13.48 | 15.34 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | 33kV system and BSP capacity constraint. | 33/11 | Red
HOLWELL |  | FROME | 6.65/25.0 | 51.199211 | -2.399832 | 15.00 | 0.00 | 1.74 | 9.51 | 1.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | 33kV system and BSP capacity constraint. | 33/11 | Red
WARMINSTER |  | FROME | 7.74/16.0 | 51.199693 | -2.217211 | 15.00 | 0.00 | 1.94 | 9.53 | 0.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constrained by BSP thermal capacity. | 33/11 | Red
WESTBURY |  | FROME | 10.00/13.1 | 51.262252 | -2.178524 | 30.00 | 0.00 | 2.30 | 13.50 | 4.76 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constrained by BSP and 33kV system thermal capacity. | 33/11 | Red
WESTBURY CEMENT |  | FROME | 8.20/8.8 | 51.271793 | -2.171823 | 4.00 | 0.00 | 1.16 | 13.42 | 0.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constrained by BSP and 33kV system thermal capacity. | 33/11 | Red
ASHTON PARK |  | NORRINGTON | 7.60/13.1 | 51.318888 | -2.186492 | 23.50 | 0.00 | 4.02 | 22.90 | 4.18 | 11.24 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
AVON RUBBER |  | NORRINGTON | 7.75/13.1 | 51.377211 | -2.138972 | 9.80 | 0.00 | 2.27 | 8.95 | 0.14 | 9.26 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
BRADFORD-ON-AVON |  | NORRINGTON | 7.23/25.0 | 51.383779 | -2.169901 | 21.80 | 0.00 | 3.50 | 11.90 | 0.13 | 15.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
BROMHAM |  | NORRINGTON | 2.71/13.1 | 51.383779 | -2.169901 | 5.00 | 0.00 | 0.33 | 2.31 | 0.40 | 0.00 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | No | Constrained due to Primary transformers limitations under FCO. | 33/11 | Red
CORSHAM |  | NORRINGTON | 7.99/13.1 | 51.458778 | -0.926984 | 13.00 | 0.00 | 2.63 | 11.28 | 2.00 | 5.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
DEVIZES |  | NORRINGTON | 8.43/13.1 | 51.348080 | -1.999951 | 27.00 | 0.00 | 6.94 | 22.59 | 1.37 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | 33kV system voltage and thermal constraints. | 33/11 | Red
EASTERTON |  | NORRINGTON | 6.27/13.1 | 51.291880 | -1.977292 | 15.00 | 0.00 | 1.10 | 9.87 | 0.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Upstream 33kV system constraints. | 33/11 | Red
MELKSHAM TOWN |  | NORRINGTON | 11.23/13.1 | 50.932907 | -1.454928 | 30.00 | 0.00 | 5.90 | 24.03 | 8.70 | 9.00 | 50 | Unconstrained |  |  | Partially Constrained |  |  | No | No | PROXIMITY TO FAULT LEVEL WHEN NORRINGTON BUS IS RUN SOLID. | 33/11 | Amber
SPRING QUARRY WEST |  | NORRINGTON | 9.53/13.1 | 51.417098 | -2.225718 | 30.00 | 0.00 | 1.30 | 11.78 | 12.00 | 15.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | Potential fault level constraint at the BSP. | 33/11 | Amber
TROWBRIDGE TOWN |  | NORRINGTON | 9.21/13.1 | 51.321346 | -2.220799 | 27.80 | 0.00 | 3.52 | 20.28 | 2.50 | 15.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | Possible fault level constraint at the BSP for new applications. | 33/11 | Amber
MARLBOROUGH SOUTH |  | WEST GRAFTON | 4.49/25.0 | 50.835650 | -0.773276 | 15.00 | 0.00 | 3.29 | 13.03 | 0.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constrained by 132kV system capacity. | 33/11 | Red
RAMSBURY |  | WEST GRAFTON | 3.84/13.1 | 51.447677 | -1.606393 | 8.00 | 0.00 | 0.77 | 3.96 | 0.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constrained by 132kV system capacity. | 33/11 | Red
TIDWORTH |  | WEST GRAFTON | 4.28/25.0 | 51.201458 | -1.655726 | 18.20 | 0.00 | 2.50 | 10.89 | 0.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constrained by 132kV system capacity. | 33/11 | Red
WEST GRAFTON VILLAGE |  | WEST GRAFTON | 7.25/13.1 | 51.341702 | -1.646063 | 9.80 | 0.00 | 0.92 | 5.05 | 0.18 | 1.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constrained by 132kV system capacity. | 33/11 | Red
CIRENCESTER TOWN |  | CIRENCESTER | 10.43/13.1 | 51.706202 | -1.961024 | 21.00 | 0.00 | 4.00 | 16.84 | 1.00 | 6.00 | 50 | Partially Constrained |  |  | Unconstrained |  |  | yes | Yes | Constrained by BSP. Future connections on Minety GSP will need ANM under N-2, due to NG SGT constraints. | 33/11 | Amber
CRICKLADE |  | CIRENCESTER | 6.21/20.0 | 51.638068 | -1.864990 | 15.00 | 0.00 | 2.05 | 8.51 | 0.00 | 0.00 | 50 | Constrained |  |  | Partially Constrained |  |  | Yes | Yes | Future connections on Minety GSP need ANM under N-2, due to NG SGT constraints. Voltage and thermal issues. | 33/11 | Red
FAIRFORD |  | CIRENCESTER | 7.59/25.0 | 51.703779 | -1.793020 | 15.00 | 0.00 | 2.07 | 8.57 | 0.00 | 6.00 | 50 | Partially Constrained |  |  | Partially Constrained |  |  | Yes | Yes | Future connections on Minety GSP need ANM under N-2, due to NG SGT constraints. Voltage issues. | 33/11 | Amber
MINETY VILLAGE |  | CIRENCESTER | 6.14/13.1 | 50.930117 | -2.055870 | 15.00 | 0.00 | 0.98 | 4.39 | 0.00 | 0.00 | 50 | Constrained |  |  | Partially Constrained |  |  | Yes | Yes | Future connections on Minety GSP will need ANM under N-2, due to NG SGT constraints. Voltage issues. | 33/11 | Red
NORTHLEACH |  | CIRENCESTER | 5.78/25.0 | 51.826681 | -1.848612 | 13.00 | 0.00 | 1.52 | 5.63 | 0.00 | 6.00 | 50 | Partially Constrained |  |  | Partially Constrained |  |  | Yes | Yes | Future connections on Minety GSP will need ANM under N-2, due to NG SGT constraints. | 33/11 | Amber
SHIPTON OLIFFE |  | CIRENCESTER | 2.89/13.1 | 51.870012 | -1.944617 | 3.90 | 0.00 | 0.79 | 3.22 | 0.00 | 4.00 | 50 | Partially Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations under FCO. Future connections on Minety GSP will need ANM under N-2, due to NG SGT constraints. | 33/11 | Red
WHITEWAY |  | CIRENCESTER | 7.83/13.1 | 50.876464 | -1.249637 | 30.00 | 0.00 | 2.20 | 10.46 | 0.00 | 0.00 | 50 | Constrained |  |  | Partially Constrained |  |  | Yes | Yes | National Grid reinforcement works required for saturated N-1 SGT capacity, estimated connection date for new applications is 2025-2026. | 33/11 | Red
DRAKES WAY |  | STRATTON MAIN | 8.22/13.1 | 51.569469 | -1.756550 | 15.00 | 0.00 | 1.81 | 8.81 | 0.00 | 15.00 | 50 | Partially Constrained |  |  | Partially Constrained |  |  | No | No | Proximity to fault rating issue when Stratton bus is run solid. Future connections on Minety GSP will need ANM under N-2, due to NG SGT constraints. | 33/11 | Amber
PARK NORTH |  | STRATTON MAIN | 9.27/13.1 | 51.559186 | -1.741026 | 30.00 | 0.00 | 5.12 | 19.11 | 1.00 | 15.00 | 50 | Partially Constrained |  |  | Partially Constrained |  |  | Yes | Yes | Proximity to fault rating issue when Stratton bus is run solid. Future connections on Minety GSP will need ANM under N-2, due to NG SGT constraints. | 33/11 | Amber
PLESSEY |  | STRATTON MAIN | 8.58/20.0 | 51.579053 | -1.764825 | 19.50 | 0.00 | 2.89 | 11.38 | 0.00 | 15.00 | 50 | Partially Constrained |  |  | Partially Constrained |  |  | Yes | Yes | Proximity to fault rating issue when Stratton bus is run solid. Future connections on Minety GSP will need ANM under N-2, due to NG SGT constraints. | 33/11 | Amber
PRESSED STEEL SWINDON |  | STRATTON MAIN | 11.89/13.1 | 51.575780 | -1.755953 | 13.00 | 0.00 | 1.88 | 9.31 | 0.00 | 11.00 | 50 | Partially Constrained |  |  | Partially Constrained |  |  | Yes | Yes | Proximity to fault rating issue when Stratton bus is run solid. Future connections on Minety GSP will need ANM under N-2, due to NG SGT constraints. | 33/11 | Amber
BLACK BOURTON |  | STRATTON RESERVE | 5.65/25.0 | 51.732288 | -1.590171 | 13.00 | 0.00 | 0.70 | 5.58 | 0.00 | 2.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Proximity to fault rating issue when Stratton bus is run solid. Future connections on Minety GSP need ANM under N-2, due to NG SGT constraints. Constrained by 33kV system capacity. | 33/11 | Red
FARINGDON |  | STRATTON RESERVE | 6.12/25.0 | 51.652247 | -1.584533 | 13.60 | 5.07 | 3.73 | 12.06 | 0.00 | 3.00 | 50 | Partially Constrained |  |  | Partially Constrained |  |  | Yes | Yes | Proximity to fault rating issue when Stratton bus is run solid. Future connections on Minety GSP will need ANM under N-2, due to NG SGT constraints. | 33/11 | Amber
LECHLADE |  | STRATTON RESERVE | 5.5/13.1 | 51.702181 | -1.681606 | 9.80 | 0.00 | 1.27 | 7.64 | 0.00 | 1.00 | 50 | Partially Constrained |  |  | Partially Constrained |  |  | Yes | Yes | Proximity to fault rating issue when Stratton bus is run solid. Future connections on Minety GSP will need ANM under N-2, due to NG SGT constraints. | 33/11 | Red
SHRIVENHAM |  | STRATTON RESERVE | 12.3/13.1 | 51.589634 | -1.657854 | 15.00 | 0.00 | 1.39 | 5.88 | 0.00 | 3.00 | 50 | Partially Constrained |  |  | Unconstrained |  |  | Yes | Yes | Proximity to fault rating issue when Stratton bus is run solid. Future connections on Minety GSP will need ANM under N-2, due to NG SGT constraints. | 33/11 | Amber
STANTON FITZWARREN |  | STRATTON RESERVE | 9.15/25.0 | 51.617285 | -1.747773 | 18.20 | 0.00 | 2.47 | 12.45 | 7.50 | 4.00 | 50 | Partially Constrained |  |  | Partially Constrained |  |  | Yes | Yes | Proximity to fault rating issue when Stratton bus is run solid. Future connections on Minety GSP will need ANM under N-2, due to NG SGT constraints. | 33/11 | Amber
STRATTON |  | STRATTON RESERVE | 10.12/13.1 | 51.597322 | -1.755564 | 30.00 | 0.00 | 4.02 | 15.71 | 5.60 | 22.00 | 50 | Partially Constrained |  |  | Partially Constrained |  |  | Yes | Yes | Proximity to fault rating issue when Stratton bus is run solid. Future connections on Minety GSP will need ANM under N-2, due to NG SGT constraints. | 33/11 | Amber
MANCHESTER ROAD |  | SWINDON | 11.66/13.1 | 51.586121 | -2.112677 | 37.00 | 0.00 | 6.10 | 27.12 | 0.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Constrained by BSP capacity. Future connections on Minety GSP will need ANM under N-2, due to NG SGT constraints. | 33/11 | Red
SWINDON |  | SWINDON | 10.45/13.1 | 51.582282 | -1.821758 | 60.00 | 0.00 | 7.85 | 31.14 | 5.66 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Constrained by BSP thermal capacity. | 33/11 | Red
TRADING ESTATE |  | SWINDON | 10.83/25.0 | 51.570909 | -1.805311 | 21.60 | 0.00 | 1.60 | 10.81 | 2.57 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Constrained by BSP capacity. Future connections on Minety GSP will need ANM under N-2, due to NG SGT constraints. | 33/11 | Red
WOOTTON BASSETT |  | SWINDON | 14.31/25.0 | 51.528671 | -1.891982 | 24.00 | 0.00 | 1.80 | 11.80 | 23.00 | 0.00 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | National Grid reinforcement works required for saturated N-1 SGT capacity, estimated connection date for new applications is 2025-2026. | 33/11 | Red
CHISLEDON |  | TOOTHILL | 7.23/25.0 | 51.518068 | -1.729009 | 15.00 | 0.00 | 1.20 | 4.25 | 0.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to upstream thermal limitations. Future connections on Minety GSP need ANM under N-2, due to NG SGT constraints. | 33/11 | Red
DORCAN SOUTH |  | TOOTHILL | 6.80/13.1 | 51.550244 | -1.723337 | 22.00 | 0.00 | 3.97 | 12.61 | 0.00 | 1.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to upstream thermal limitations. Future connections on Minety GSP will need ANM under N-2, due to NG SGT constraints. | 33/11 | Red
QUARRY ROAD |  | TOOTHILL | 12.7/13.1 | 51.549105 | -1.779733 | 23.12 | 0.00 | 3.97 | 18.39 | 1.80 | 1.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Proximity to fault rating. Constrained due to upstream thermal limitations. Future connections on Minety GSP will need ANM under N-2, due to NG SGT constraints. | 33/11 | Red
TOOTHILL |  | TOOTHILL | 14.75/18.4 | 51.555003 | -1.810859 | 60.00 | 0.00 | 4.35 | 25.52 | 2.06 | 1.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to upstream thermal limitations. No spare bay. Future connections on Minety GSP will need ANM under N-2, due to NG SGT constraints. | 33/11 | Red
WROUGHTON |  | TOOTHILL | 10.67/13.1 | 51.531597 | -1.793801 | 24.00 | 0.00 | 2.04 | 7.10 | 11.00 | 0.00 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | National Grid reinforcement works required for saturated N-1 SGT capacity, estimated connection date for new applications is 2025-2026. | 33/11 | Red
BATH ROAD EAST |  | NORTH HYDE (D) | 5.43/13.1 | 51.480253 | -0.430027 | 13.00 | 0.00 | 2.84 | 12.79 | 0.00 | 15.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/11 | Green
SPRINGFIELD ROAD |  | NORTH HYDE (D) | 11.21/13.1 | 51.513970 | -0.395144 | 27.40 | 0.00 | 4.24 | 17.71 | 0.00 | 24.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/6.6 | Green
THE GREEN |  | NORTH HYDE (D) | 9.16/13.1 | 51.503172 | -0.381548 | 12.00 | 0.00 | 2.06 | 10.85 | 0.00 | 14.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/6.6 | Green
BASSETT |  | ROWNHAMS | 11.06/13.1 | 50.935016 | -1.390437 | 30.00 | 0.00 | 3.41 | 18.49 | 0.23 | 33.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
BEVOIS VALLEY |  | ROWNHAMS | 8.3/25.0 | 50.916514 | -1.394804 | 22.90 | 0.00 | 2.95 | 14.64 | 1.18 | 24.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/6.6 | Green
BISHOPSTOKE |  | ROWNHAMS | 8.78/13.1 | 50.964778 | -1.340207 | 13.00 | 0.00 | 1.84 | 7.34 | 0.00 | 14.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
CENTRAL BRIDGE |  | ROWNHAMS | 10.27/25.0 | 50.899163 | -1.395598 | 40.00 | 0.00 | 4.15 | 20.23 | 0.00 | 44.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
CHANDLERS FORD |  | ROWNHAMS | 8.41/25.0 | 50.991533 | -1.381861 | 30.00 | 0.00 | 2.77 | 13.34 | 0.00 | 32.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
CHAPEL |  | ROWNHAMS | 13.6/25.0 | 50.905438 | -1.391819 | 15.00 | 0.00 | 2.73 | 12.40 | 0.00 | 17.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/6.6 | Green
DUNBRIDGE |  | ROWNHAMS | 5.15/13.1 | 51.034391 | -1.551430 | 9.80 | 0.00 | 2.02 | 8.39 | 0.04 | 0.00 | 50 | Partially Constrained |  |  | Unconstrained |  |  | No | Yes | Proximity to voltage issues. | 33/11 | Amber
EASTLEIGH NORTH |  | SOUTHAMPTON MAIN | 10.92/16.0 | 50.968085 | -1.354373 | 40.00 | 0.00 | 7.03 | 28.84 | 3.92 | 43.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
FLETCHWOOD |  | SOUTHAMPTON MAIN | 7.7/25.0 | 50.907385 | -1.520224 | 30.00 | 0.00 | 4.15 | 17.81 | 0.00 | 31.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
GORDON ROAD |  | SOUTHAMPTON MAIN | 8.05/25.0 | 51.067319 | -1.313918 | 30.00 | 0.00 | 5.70 | 23.25 | 0.00 | 0.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
HARESTOCK |  | SOUTHAMPTON MAIN | 7.31/25.0 | 51.079097 | -1.345007 | 24.30 | 0.00 | 4.54 | 16.57 | 0.47 | 0.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
HEDGE END |  | SOUTHAMPTON RESERVE | 6.3/20.0 | 51.769341 | -1.212263 | 14.20 | 0.00 | 2.09 | 10.79 | 0.00 | 16.00 | 50 | Unconstrained |  |  | Unconstrained | Split Hedge End-Bishops Waltham | 30/01/20 | No | Yes | None known | 33/11 | Green
HOUGHTON |  | SOUTHAMPTON RESERVE | 3.42/25.0 | 51.084980 | -1.519532 | 9.80 | 0.00 | 1.33 | 6.48 | 0.00 | 0.00 | 50 | Partially Constrained |  |  | Unconstrained |  |  | No | Yes | Proximity to voltage issues. | 33/11 | Amber
LORDSHILL |  | SOUTHAMPTON RESERVE | 11.64/13.1 | 50.942596 | -1.450118 | 30.00 | 0.00 | 2.95 | 11.73 | 0.00 | 28.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
MAYBUSH |  | VELMORE | 13.21/25 | 51.413842 | -1.723154 | 26.00 | 0.00 | 4.66 | 18.30 | 2.00 | 28.00 | 50 | Unconstrained |  |  | Unconstrained | Maybush-E switchgear reinforcement | 01/03/21 | No | Yes | None known | 33/11 | Green
NORTH BADDESLEY |  | VELMORE | 10.55/13.1 | 50.982918 | -1.457905 | 19.50 | 0.00 | 3.75 | 14.86 | 0.00 | 23.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
REGENTS PARK |  | VELMORE | 8.78/13.1 | 50.915674 | -1.442754 | 30.00 | 0.00 | 3.70 | 12.66 | 1.20 | 32.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
ROMSEY |  | VELMORE | 8.37/13.1 | 50.988175 | -1.487050 | 21.00 | 0.00 | 2.73 | 16.05 | 0.00 | 7.10 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | Moderate proximity to 33kV circts limitations under FCO. | 33/11 | Green
SHIRLEY |  | VELMORE | 8.35/25.0 | 50.922458 | -1.432287 | 30.00 | 0.00 | 3.84 | 16.17 | 0.00 | 33.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
SILKSTEAD |  | VELMORE | 5.3/13.1 | 51.018246 | -1.366109 | 13.00 | 0.00 | 1.56 | 7.36 | 2.07 | 12.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
ST CROSS |  | WINCHESTER | 10.24/13.1 | 51.051026 | -1.326428 | 26.00 | 0.00 | 4.45 | 17.27 | 0.06 | 0.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
TOTTON |  | WINCHESTER | 10.84/13.1 | 50.919204 | -1.491294 | 24.50 | 0.00 | 4.27 | 15.26 | 2.00 | 26.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
VELMORE |  | WINCHESTER | 8.94/18.4 | 50.970764 | -1.391038 | 30.00 | 0.00 | 7.84 | 24.34 | 1.50 | 36.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/11 | Green
WESTERN ESPLANADE |  | WINCHESTER | 12.4/13.1 | 50.906374 | -1.409528 | 60.00 | 0.00 | 9.38 | 33.06 | 0.36 | 69.00 | 50 | Unconstrained |  |  | Partially Constrained |  |  | No | Yes | Moderate proximity to fault rating. | 33/11 | Amber
WOODMILL LANE |  | WINCHESTER | 11.48/25.0 | 50.936664 | -1.379030 | 24.00 | 0.00 | 1.96 | 8.85 | 0.00 | 25.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | None known | 33/6.6 | Green
CANAL BANK 6.6KV |  | ACTON LANE | 12.32/13.1 | 51.532509 | -0.257524 | 14.90 | 0.00 | 0.70 | 8.80 | 0.00 | 15.00 | 50 | Unconstrained |  |  | Partially Constrained |  |  | No | No | Moderate proximity to fault rating. | 66/11 | Amber
GOLDSMITHS |  | ACTON LANE | 11.91/13.1 | 51.512702 | -0.255973 | 13.00 | 0.00 | 1.82 | 10.32 | 0.00 | 14.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/6.6 | Green
LEAMINGTON PARK |  | ACTON LANE | 12.13/13.1 | 51.520012 | -0.263766 | 13.00 | 0.00 | 2.50 | 11.86 | 0.00 | 15.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/6.6 | Green
PARK ROYAL |  | ACTON LANE | 11.98/13.1 | 51.526116 | -0.269156 | 12.80 | 0.00 | 2.30 | 10.82 | 0.00 | 15.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/6.6 | Green
CANAL BANK 11KV |  | GREENFORD | 15.29/25.0 | 51.533591 | -0.257771 | 60.00 | 0.00 | 16.30 | 45.65 | 0.00 | 74.00 | 50 | Unconstrained |  |  | Partially Constrained |  |  | No | No | None known | 22/6.6 | Amber
GREENFORD |  | GREENFORD | 10.94/20.0 | 51.541275 | -0.347606 | 60.00 | 0.00 | 14.98 | 45.87 | 1.00 | 73.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/11 | Green
PERIVALE |  | PERIVALE | 13.48/25.0 | 51.533318 | -0.306658 | 40.00 | 0.00 | 9.54 | 28.84 | 0.00 | 49.00 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/11 | Green

## Contracted Generator
Project Name | Corresponding GSP | Corresponding BSP | Corresponding PSS | Technology Type | Voltage (kV) | Status | Contracted Capacity (MVA) | Connection Date
FLACKWELL HEATH PROJECT_1 | AMERSHAM |  |  | LANDFILL GAS | 11kV | CONNECTED | 1.4
LOUDWATER PROJECT_2 | AMERSHAM |  |  | BATTERY | 33kV | ACCEPTED | 40
WELL END PROJECT_3 | AMERSHAM |  |  | BATTERY | 11kV | ACCEPTED | 7.2
AXMINSTER PROJECT_18 | AXMINSTER |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 35
AXMINSTER PROJECT_19 | AXMINSTER |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 35
AXMINSTER PROJECT_25 | AXMINSTER |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 30
CASTLE CARY PROJECT_12 | AXMINSTER |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.32
CASTLE CARY PROJECT_4 | AXMINSTER |  |  | LANDFILL GAS | 11kV | CONNECTED | 3.8
CHILTON CANTELLO PROJECT_5 | AXMINSTER |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
HENSTRIDGE PROJECT_11 | AXMINSTER |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.13
HENSTRIDGE PROJECT_13 | AXMINSTER |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.1
MILBORNE PORT PROJECT_20 | AXMINSTER |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
SPARKFORD PROJECT_14 | AXMINSTER |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.2
YEOVIL PROJECT_10 | AXMINSTER |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.13
YEOVIL PROJECT_21 | AXMINSTER |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 9
YEOVIL PROJECT_22 | AXMINSTER |  |  | CHP - GAS TURBINE | 33kV | ACCEPTED | 15
YEOVIL PROJECT_23 | AXMINSTER |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 7.6
YEOVIL PROJECT_24 | AXMINSTER |  |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 10
YEOVIL PROJECT_6 | AXMINSTER |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10.59
YEOVIL PROJECT_7 | AXMINSTER |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8.8
YEOVIL PROJECT_8 | AXMINSTER |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5.55
YEOVIL PROJECT_9 | AXMINSTER |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7.5
YETMINSTER PROJECT_15 | AXMINSTER |  |  | DIESEL | 11kV | CONNECTED | 0.4
YETMINSTER PROJECT_16 | AXMINSTER |  |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0.25
YETMINSTER PROJECT_17 | AXMINSTER |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.15
BISHOPS WALTHAM PROJECT_27 | BOTLEY WOOD GSP |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
BISHOPS WALTHAM PROJECT_686 | BOTLEY WOOD GSP |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 2.5
BOTLEY WOOD PROJECT_29 | BOTLEY WOOD GSP |  |  | LANDFILL GAS | 33kV | ACCEPTED | 14
BOTLEY WOOD PROJECT_30 | BOTLEY WOOD GSP |  |  | DIESEL | 33kV | CONNECTED | 20
BOTLEY WOOD PROJECT_558 | BOTLEY WOOD GSP |  |  | BATTERY | 33kV | ACCEPTED | 49.9
HAMBLE PROJECT_33 | BOTLEY WOOD GSP |  |  | BATTERY | 11kV | ACCEPTED | 5
HAMBLE PROJECT_585 | BOTLEY WOOD GSP |  |  | LANDFILL GAS | 11kV | ACCEPTED | 7.2
NETLEY COMMON PROJECT_28 | BOTLEY WOOD GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12
NETLEY COMMON PROJECT_31 | BOTLEY WOOD GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
WESTON PROJECT_26 | BOTLEY WOOD GSP |  |  | LANDFILL GAS | 11kV | CONNECTED | 2.6
AMESBURY PROJECT_410 | BRAMLEY (ANDO-THAT) |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5.64
AMESBURY PROJECT_412 | BRAMLEY (ANDO-THAT) |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.6
AMESBURY PROJECT_446 | BRAMLEY (ANDO-THAT) |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 3.5
BEENHAM PROJECT_54 | BRAMLEY (ANDO-THAT) |  |  | LANDFILL GAS | 11kV | CONNECTED | 1.9
BOSCOMBE DOWN PROJECT_441 | BRAMLEY (ANDO-THAT) |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 10
BOSCOMBE DOWN PROJECT_454 | BRAMLEY (ANDO-THAT) |  |  | DIESEL | 11kV | CONNECTED | 4
BRAMLEY (ANDO-THAT) PROJECT_560 | BRAMLEY (ANDO-THAT) |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 40
BRAMLEY (ANDO-THAT) PROJECT_599 | BRAMLEY (ANDO-THAT) |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 15.79
BRAMLEY (ANDO-THAT) PROJECT_600 | BRAMLEY (ANDO-THAT) |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 21.05
KINTBURY PROJECT_56 | BRAMLEY (ANDO-THAT) |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.2
TADLEY PROJECT_62 | BRAMLEY (ANDO-THAT) |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.3
THATCHAM PROJECT_49 | BRAMLEY (ANDO-THAT) |  |  | NATURAL GAS | 11kV | CONNECTED | 9.6
THATCHAM PROJECT_50 | BRAMLEY (ANDO-THAT) |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.7
THATCHAM PROJECT_57 | BRAMLEY (ANDO-THAT) |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 14
THATCHAM PROJECT_58 | BRAMLEY (ANDO-THAT) |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 16
THATCHAM PROJECT_65 | BRAMLEY (ANDO-THAT) |  |  | GAS TURBINE | 33kV | ACCEPTED | 20.53
ARBORFIELD PROJECT_34 | BRAMLEY (BASI) |  |  | LANDFILL GAS | 11kV | CONNECTED | 1
ARBORFIELD PROJECT_35 | BRAMLEY (BASI) |  |  | OTHER SYNCHRONOUS | 11kV | CONNECTED | 1.44
BASINGSTOKE PROJECT_36 | BRAMLEY (BASI) |  |  | WASTE TO ENERGY | 11kV | CONNECTED | 12
BASINGSTOKE PROJECT_37 | BRAMLEY (BASI) |  |  | OTHER SYNCHRONOUS | 11kV | CONNECTED | 0.75
BASINGSTOKE T1A & T2A PROJECT_41 | BRAMLEY (BASI) |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4
BASINGSTOKE T1A & T2A PROJECT_42 | BRAMLEY (BASI) |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 3
BASINGSTOKE T1A & T2A PROJECT_559 | BRAMLEY (BASI) |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 14.2
BASINGSTOKE T1B & T2B PROJECT_44 | BRAMLEY (BASI) |  |  | GAS TURBINE | 33kV | CONNECTED | 16
BASINGSTOKE T1B & T2B PROJECT_603 | BRAMLEY (BASI) |  |  | BATTERY | 33kV | ACCEPTED | 25
BASINGSTOKE T3 & T4 PROJECT_47 | BRAMLEY (BASI) |  |  | BATTERY | 33kV | ACCEPTED | 20
BASINGSTOKE T3 & T4 PROJECT_654 | BRAMLEY (BASI) |  |  | PV & BATTERY | 33kV | ACCEPTED | 31.58
BRAMLEY (BASI) PROJECT_601 | BRAMLEY (BASI) |  |  | BATTERY | 132kV | ACCEPTED | 99.9
CHINEHAM PROJECT_45 | BRAMLEY (BASI) |  |  | CHP - GAS TURBINE | 11kV | CONNECTED | 1.368
HOUNDMILLS PROJECT_38 | BRAMLEY (BASI) |  |  | NATURAL GAS | 11kV | CONNECTED | 1.3
HOUNDMILLS PROJECT_40 | BRAMLEY (BASI) |  |  | DIESEL | 11kV | CONNECTED | 1.2
JAYS CLOSE PROJECT_46 | BRAMLEY (BASI) |  |  | DIESEL | 11kV | CONNECTED | 4
OVERTON PROJECT_39 | BRAMLEY (BASI) |  |  | NATURAL GAS | 11kV | CONNECTED | 7.2
OVERTON PROJECT_43 | BRAMLEY (BASI) |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3.2
OVERTON PROJECT_605 | BRAMLEY (BASI) |  |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 1.2
CHICKERELL PROJECT_661 | CHICKERELL GSP |  |  | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.069
CHICKERELL PROJECT_67 | CHICKERELL GSP |  |  | NATURAL GAS | 33kV | CONNECTED | 47.8
CHICKERELL PROJECT_670 | CHICKERELL GSP |  |  | WASTE TO ENERGY | 33kV | ACCEPTED | 15.2
CHICKERELL PROJECT_692 | CHICKERELL GSP |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.7
CHICKERELL PROJECT_695 | CHICKERELL GSP |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2.2
CHICKERELL PROJECT_72 | CHICKERELL GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7.2
CHICKERELL PROJECT_73 | CHICKERELL GSP |  |  | ANAEROBIC DIGESTER | 33kV | CONNECTED | 1.3
CHICKERELL PROJECT_76 | CHICKERELL GSP |  |  | BATTERY | 33kV | ACCEPTED | 10
CHICKERELL PROJECT_77 | CHICKERELL GSP |  |  | BATTERY | 33kV | ACCEPTED | 5
DORCHESTER PROJECT_671 | CHICKERELL GSP |  |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 0
DORCHESTER PROJECT_68 | CHICKERELL GSP |  |  | NATURAL GAS | 11kV | CONNECTED | 1.44
DORCHESTER PROJECT_710 | CHICKERELL GSP |  |  | ANAEROBIC DIGESTER | 11kV | CONNECTED | 0.36
DORCHESTER PROJECT_74 | CHICKERELL GSP |  |  | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.095
DORCHESTER PROJECT_75 | CHICKERELL GSP |  |  | CHP - GAS TURBINE | 0.4kV | ACCEPTED | 0.1
PORTLAND PROJECT_69 | CHICKERELL GSP |  |  | DIESEL | 11kV | CONNECTED | 2.4
WEYMOUTH PROJECT_70 | CHICKERELL GSP |  |  | NATURAL GAS | 11kV | CONNECTED | 3.02
WINTERBOURNE KINGSTON PROJECT_371 | CHICKERELL GSP |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.124
ARNCOTT PROJECT_102 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7.2
ARNCOTT PROJECT_124 | COWLEY |  |  | GAS TURBINE | 11kV | ACCEPTED | 5
BERINSFIELD PROJECT_100 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2
BERINSFIELD PROJECT_109 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.14
BLEDINGTON PROJECT_110 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.188
CHARLBURY PROJECT_108 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 4.3
CHARLBURY PROJECT_621 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.078
CHIPPING NORTON PROJECT_613 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.05
CHOLSEY PROJECT_619 | COWLEY |  |  | LANDFILL GAS | 11kV | CONNECTED | 0.05
CHOLSEY PROJECT_623 | COWLEY |  |  | LANDFILL GAS | 11kV | CONNECTED | 0.25
COWLEY LOCAL MAIN PROJECT_129 | COWLEY |  |  | BATTERY | 33kV | ACCEPTED | 11
COWLEY LOCAL PROJECT_118 | COWLEY |  |  | DIESEL | 11kV | CONNECTED | 0.56
COWLEY LOCAL PROJECT_620 | COWLEY |  |  | OTHER SYNCHRONOUS | 11kV | CONNECTED | 0.149
COWLEY LOCAL RESERVE PROJECT_586 | COWLEY |  |  | PV & BATTERY | 33kV | ACCEPTED | 50
COWLEY LOCAL RESERVE PROJECT_98 | COWLEY |  |  | GAS TURBINE | 33kV | CONNECTED | 12
COWLEY PROJECT_126 | COWLEY |  |  | GAS TURBINE | 132kV | ACCEPTED | 49.99
COWLEY PROJECT_128 | COWLEY |  |  | GAS TURBINE | 132kV | ACCEPTED | 99.99
COWLEY PROJECT_567 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 50
COWLEY PROJECT_633 | COWLEY |  |  | DIESEL | 11kV | CONNECTED | 2.01
COWLEY PROJECT_639 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.1
COWLEY PROJECT_640 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.1
COWLEY PROJECT_644 | COWLEY |  |  | WIND FARM | 11kV | CONNECTED | 0.014
COWLEY PROJECT_646 | COWLEY |  |  | DIESEL | 11kV | ACCEPTED | 0.001
COWLEY PROJECT_80 | COWLEY |  |  | GAS TURBINE | 132kV | CONNECTED | 100
DEDDINGTON PROJECT_650 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.05
DRAYTON PROJECT_1 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 20
DRAYTON PROJECT_101 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 21.25
DRAYTON PROJECT_125 | COWLEY |  |  | GAS TURBINE | 33kV | ACCEPTED | 13
DRAYTON PROJECT_2 | COWLEY |  |  | GAS TURBINE | 33kV | ACCEPTED | 18
DRAYTON PROJECT_86 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
DRAYTON PROJECT_89 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 14.1
DRAYTON PROJECT_95 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 35
DRAYTON PROJECT_96 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12.2
EYNSHAM PROJECT_92 | COWLEY |  |  | DIESEL | 11kV | CONNECTED | 1
FULSCOT PROJECT_131 | COWLEY |  |  | LANDFILL GAS | 11kV | ACCEPTED | 7.56
HEADINGTON PROJECT_103 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12
HEADINGTON PROJECT_132 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 13
HEADINGTON PROJECT_141 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
HEADINGTON PROJECT_582 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 18
HEADINGTON PROJECT_93 | COWLEY |  |  | CHP - GAS TURBINE | 11kV | CONNECTED | 3.6
HEADINGTON PROJECT_94 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
HIGH WYCOMBE PROJECT_628 | COWLEY |  |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0.07
HIGH WYCOMBE PROJECT_84 | COWLEY |  |  | LANDFILL GAS | 11kV | CONNECTED | 1
KENNINGTON PROJECT_622 | COWLEY |  |  | SMALL HYDRO | 11kV | CONNECTED | 0.4
KIDDINGTON PROJECT_624 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.179
MILTON PROJECT_612 | COWLEY |  |  | LANDFILL GAS | 11kV | CONNECTED | 0.45
MILTON PROJECT_626 | COWLEY |  |  | SMALL HYDRO | 11kV | CONNECTED | 0.406
MILTON PROJECT_645 | COWLEY |  |  | DIESEL | 11kV | CONNECTED | 1
MILTON PROJECT_649 | COWLEY |  |  | DIESEL | 11kV | ACCEPTED | 0.001
MILTON PROJECT_81 | COWLEY |  |  | DIESEL | 11kV | CONNECTED | 3.3
MILTON PROJECT_91 | COWLEY |  |  | OTHER SYNCHRONOUS | 11kV | CONNECTED | 1.68
NORTH HINKSEY PROJECT_618 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.3
OLD ROAD PROJECT_635 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.344
OSNEY PROJECT_636 | COWLEY |  |  | DIESEL | 11kV | CONNECTED | 0.504
OXFORD PROJECT_634 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.21
OXFORD PROJECT_642 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.2
OXFORD PROJECT_643 | COWLEY |  |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0.02
ROSE HILL PROJECT_641 | COWLEY |  |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0.8
ST EBBES PROJECT_631 | COWLEY |  |  | DIESEL | 11kV | CONNECTED | 0.2
ST EBBES PROJECT_632 | COWLEY |  |  | DIESEL | 11kV | CONNECTED | 0.5
STANDLAKE PROJECT_85 | COWLEY |  |  | LANDFILL GAS | 11kV | CONNECTED | 2
WALLINGFORD PROJECT_121 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.05
WALLINGFORD PROJECT_610 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.684
WALLINGFORD PROJECT_614 | COWLEY |  |  | LANDFILL GAS | 11kV | CONNECTED | 2.4
WALLINGFORD PROJECT_99 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.36
WANTAGE PROJECT_616 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.05
WATLINGTON PROJECT_104 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 17
WHEATLEY PROJECT_570 | COWLEY |  |  | NATURAL GAS | 11kV | ACCEPTED | 7.12
WINDRUSH PARK PROJECT_637 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.03
WINSMORE LANE PROJECT_647 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.001
WITNEY & YARNTON PROJECT_105 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 11.85
WITNEY & YARNTON PROJECT_106 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12.5
WITNEY & YARNTON PROJECT_107 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
WITNEY & YARNTON PROJECT_113 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.95
WITNEY & YARNTON PROJECT_127 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 6
WITNEY & YARNTON PROJECT_565 | COWLEY |  |  | PV & BATTERY | 33kV | ACCEPTED | 13.5
WITNEY & YARNTON PROJECT_566 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 21.5
WITNEY & YARNTON PROJECT_592 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 18
WITNEY & YARNTON PROJECT_617 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.05
WITNEY & YARNTON PROJECT_627 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.05
WITNEY & YARNTON PROJECT_629 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.015
WITNEY & YARNTON PROJECT_630 | COWLEY |  |  | CHP - GAS TURBINE | 11kV | CONNECTED | 1
WITNEY & YARNTON PROJECT_88 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 35
WOODSTOCK PROJECT_611 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.51
WOOTTON ROAD PROJECT_615 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.24
YARNTON PROJECT_114 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 4.98
BOSTON MANOR PROJECT_133 | EALING |  |  | OTHER SYNCHRONOUS | 11kV | CONNECTED | 7.5
BOSTON MANOR PROJECT_135 | EALING |  |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 1
HARVARD LANE PROJECT_136 | EALING |  |  | GAS TURBINE | 11kV | CONNECTED | 1.6
IRONBRIDGE PROJECT_134 | EALING |  |  | DIESEL | 11kV | CONNECTED | 1.012
BICESTER NORTH PROJECT_568 | EAST CLAYDON |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 44
BICESTER NORTH PROJECT_638 | EAST CLAYDON |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.499
BICESTER NORTH PROJECT_90 | EAST CLAYDON |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 17.16
BICESTER PROJECT_111 | EAST CLAYDON |  |  | CHP - GAS TURBINE | 11kV | CONNECTED | 3.169
BICESTER PROJECT_117 | EAST CLAYDON |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.899
BICESTER PROJECT_142 | EAST CLAYDON |  |  | CHP - GAS TURBINE | 11kV | CONNECTED | 3.169
BICESTER PROJECT_625 | EAST CLAYDON |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.023
BICESTER PROJECT_648 | EAST CLAYDON |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.001
BICESTER PROJECT_651 | EAST CLAYDON |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.25
BICESTER PROJECT_97 | EAST CLAYDON |  |  | WASTE TO ENERGY | 33kV | CONNECTED | 26
COTTISFORD PROJECT_139 | EAST CLAYDON |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
COTTISFORD PROJECT_87 | EAST CLAYDON |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
EAST CLAYDON PROJECT_587 | EAST CLAYDON |  |  | BATTERY | 132kV | ACCEPTED | 40
UPPER HEYFORD PROJECT_116 | EAST CLAYDON |  |  | LANDFILL GAS | 11kV | CONNECTED | 1.57
UPPER HEYFORD PROJECT_119 | EAST CLAYDON |  |  | LANDFILL GAS | 11kV | ACCEPTED | 1
UPPER HEYFORD PROJECT_143 | EAST CLAYDON |  |  | LANDFILL GAS | 11kV | CONNECTED | 1.57
UPPER HEYFORD PROJECT_83 | EAST CLAYDON |  |  | LANDFILL GAS | 11kV | CONNECTED | 3.25
BINSTEAD PROJECT_175 | FAWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.85
BUTTS ASH PROJECT_149 | FAWLEY |  |  | LANDFILL GAS | 11kV | CONNECTED | 11.5
COWES & WOOTTON COMMON PROJECT_146 | FAWLEY |  |  | NATURAL GAS | 33kV | CONNECTED | 33
COWES & WOOTTON COMMON PROJECT_152 | FAWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8.8
COWES & WOOTTON COMMON PROJECT_153 | FAWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
COWES & WOOTTON COMMON PROJECT_154 | FAWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
COWES & WOOTTON COMMON PROJECT_159 | FAWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
COWES & WOOTTON COMMON PROJECT_165 | FAWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8.1
COWES & WOOTTON COMMON PROJECT_730 | FAWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.003
COWES PROJECT_164 | FAWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3.5
FAWLEY PROJECT_ | FAWLEY |  |  | BATTERY | 132kV | ACCEPTED | 48
FAWLEY PROJECT_150 | FAWLEY |  |  | GAS TURBINE | 132kV | CONNECTED | 76.565
FAWLEY PROJECT_155 | FAWLEY |  |  | OIL | 132kV | CONNECTED | 140
FAWLEY PROJECT_156 | FAWLEY |  |  | OIL | 132kV | CONNECTED | 145
FAWLEY PROJECT_157 | FAWLEY |  |  | OIL | 132kV | CONNECTED | 145
FAWLEY PROJECT_158 | FAWLEY |  |  | OIL | 132kV | CONNECTED | 145
FRESHWATER PROJECT_171 | FAWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.2
FRESHWATER PROJECT_172 | FAWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.25
LANGLEY PROJECT_161 | FAWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
LANGLEY PROJECT_170 | FAWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3
LANGLEY PROJECT_715 | FAWLEY |  |  | OTHER SYNCHRONOUS | 11kV | ACCEPTED | 0.33
NEWPORT PROJECT_147 | FAWLEY |  |  | LANDFILL GAS | 11kV | CONNECTED | 1.2
NEWPORT PROJECT_148 | FAWLEY |  |  | NATURAL GAS | 11kV | CONNECTED | 2.5
NEWPORT PROJECT_169 | FAWLEY |  |  | NATURAL GAS | 11kV | CONNECTED | 0.65
NEWPORT PROJECT_173 | FAWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.25
NEWPORT PROJECT_174 | FAWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.25
NEWPORT PROJECT_177 | FAWLEY |  |  | NATURAL GAS | 11kV | CONNECTED | 0.5
RYDE PROJECT_151 | FAWLEY |  |  | NATURAL GAS | 11kV | CONNECTED | 1.25
SANDOWN PROJECT_176 | FAWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.98
SHALFLEET PROJECT_162 | FAWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.5
SHALFLEET PROJECT_718 | FAWLEY |  |  | WIND FARM | 11kV | ACCEPTED | 0.25
SHANKLIN PROJECT_163 | FAWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2.8
WOOTTON COMMON PROJECT_166 | FAWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6.89
WOOTTON COMMON PROJECT_167 | FAWLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
ALDERSHOT PROJECT_179 | FLEET BRAMLEY |  |  | LANDFILL GAS | 11kV | CONNECTED | 2.4
ALTON & FERNHURST PROJECT_184 | FLEET BRAMLEY |  |  | NATURAL GAS | 33kV | CONNECTED | 15
ALTON & FERNHURST PROJECT_195 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
ALTON & FERNHURST PROJECT_196 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7.92
ALTON & FERNHURST PROJECT_202 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
ALTON & FERNHURST PROJECT_203 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8.3
ALTON & FERNHURST PROJECT_211 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
ALTON & FERNHURST PROJECT_240 | FLEET BRAMLEY |  |  | NATURAL GAS | 33kV | ACCEPTED | 20
ALTON & FERNHURST PROJECT_602 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 9.975
ALTON LOCAL PROJECT_197 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.25
BRACKNELL MAIN PROJECT_212 | FLEET BRAMLEY |  |  | DIESEL | 33kV | CONNECTED | 20
BRACKNELL MAIN PROJECT_217 | FLEET BRAMLEY |  |  | GAS TURBINE | 33kV | CONNECTED | 20
BRACKNELL RESERVE PROJECT_189 | FLEET BRAMLEY |  |  | NATURAL GAS | 33kV | CONNECTED | 47.5
BRAYWICK ROAD PROJECT_224 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.075
BURGHFIELD MAIN PROJECT_200 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
CAMBERLEY PROJECT_235 | FLEET BRAMLEY |  |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 0
COURAGES PROJECT_187 | FLEET BRAMLEY |  |  | WIND FARM | 11kV | CONNECTED | 2.2
COURAGES PROJECT_193 | FLEET BRAMLEY |  |  | DIESEL | 11kV | ACCEPTED | 1.5
COURAGES PROJECT_218 | FLEET BRAMLEY |  |  | DIESEL | 11kV | ACCEPTED | 2
COXMOOR WOOD PROJECT_205 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.3
COXMOOR WOOD PROJECT_213 | FLEET BRAMLEY |  |  | NATURAL GAS | 33kV | CONNECTED | 16
COXMOOR WOOD PROJECT_214 | FLEET BRAMLEY |  |  | NATURAL GAS | 33kV | CONNECTED | 16
COXMOOR WOOD PROJECT_223 | FLEET BRAMLEY |  |  | NATURAL GAS | 33kV | ACCEPTED | 16
COXMOOR WOOD PROJECT_229 | FLEET BRAMLEY |  |  | PV & BATTERY | 33kV | CONNECTED | 6.2
FIVE OAKS PROJECT_180 | FLEET BRAMLEY |  |  | NATURAL GAS | 11kV | CONNECTED | 6.4
FIVE OAKS PROJECT_181 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
FLEET BRAMLEY PROJECT_231 | FLEET BRAMLEY |  |  | BATTERY | 132kV | ACCEPTED | 99.9
FLEET BRAMLEY PROJECT_242 | FLEET BRAMLEY |  |  | GAS TURBINE | 132kV | ACCEPTED | 99.9
FLEET BRAMLEY PROJECT_652 | FLEET BRAMLEY |  |  | PV & BATTERY | 132kV | ACCEPTED | 49.9
FRIMLEY PROJECT_190 | FLEET BRAMLEY |  |  | LANDFILL GAS | 11kV | CONNECTED | 1.4
GORING PROJECT_222 | FLEET BRAMLEY |  |  | NATURAL GAS | 11kV | ACCEPTED | 0.36
HERRIARD PROJECT_182 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
HERRIARD PROJECT_216 | FLEET BRAMLEY |  |  | ANAEROBIC DIGESTER | 11kV | CONNECTED | 2.4
HITCHES LANE PROJECT_199 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.26
LANGLEY COURT PROJECT_608 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.217
MAIDENHEAD PROJECT_206 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 0.143
MIDHURST PROJECT_185 | FLEET BRAMLEY |  |  | NATURAL GAS | 11kV | CONNECTED | 5
MILFORD PROJECT_198 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.177
MVEE PROJECT_186 | FLEET BRAMLEY |  |  | LANDFILL GAS | 11kV | CONNECTED | 1.33
MVEE PROJECT_194 | FLEET BRAMLEY |  |  | ANAEROBIC DIGESTER | 11kV | CONNECTED | 2.38
NORTHUMBERLAND AVENUE PROJECT_191 | FLEET BRAMLEY |  |  | LANDFILL GAS | 11kV | CONNECTED | 3
PETERSFIELD PROJECT_204 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.25
PLAISTOW PROJECT_655 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.322
PRESTON CANDOVER PROJECT_609 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 20
READING PROJECT_201 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.08
READING PROJECT_226 | FLEET BRAMLEY |  |  | SMALL HYDRO | 11kV | ACCEPTED | 0.1
READING PROJECT_227 | FLEET BRAMLEY |  |  | DIESEL | 11kV | ACCEPTED | 0.44
READING PROJECT_228 | FLEET BRAMLEY |  |  | DIESEL | 11kV | ACCEPTED | 0.6
READING PROJECT_230 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 11
READING TOWN PROJECT_208 | FLEET BRAMLEY |  |  | ANAEROBIC DIGESTER | 11kV | CONNECTED | 0.5
SILVER STREET PROJECT_192 | FLEET BRAMLEY |  |  | DIESEL | 11kV | ACCEPTED | 7
SOUTHCOTE PROJECT_221 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.21
THE MALL PROJECT_209 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.149
THEALE PROJECT_219 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.25
THEALE PROJECT_220 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.06
TONGHAM PROJECT_178 | FLEET BRAMLEY |  |  | LANDFILL GAS | 11kV | CONNECTED | 1.33
TONGHAM PROJECT_215 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.41
TRASH GREEN PROJECT_207 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.7
TWYFORD PROJECT_225 | FLEET BRAMLEY |  |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 0.1
WRECCLESHAM PROJECT_232 | FLEET BRAMLEY |  |  | BATTERY | 33kV | ACCEPTED | 20
CHALVEY PROJECT_251 | IVER 132KV |  |  | LANDFILL GAS | 11kV | CONNECTED | 2.5
CHALVEY PROJECT_576 | IVER 132KV |  |  | BATTERY | 33kV | ACCEPTED | 49.5
CHALVEY PROJECT_606 | IVER 132KV |  |  | BATTERY | 11kV | ACCEPTED | 6.3
DENHAM PROJECT_255 | IVER 132KV |  |  | BATTERY | 22kV | ACCEPTED | 20
DENHAM PROJECT_259 | IVER 132KV |  |  | GAS TURBINE | 22kV | ACCEPTED | 20
FARNHAM ROYAL PROJECT_246 | IVER 132KV |  |  | WASTE TO ENERGY | 11kV | CONNECTED | 12
LONGFORD PROJECT_245 | IVER 132KV |  |  | WASTE TO ENERGY | 33kV | CONNECTED | 45.7
PETERSFIELD AVENUE PROJECT_243 | IVER 132KV |  |  | NATURAL GAS | 11kV | CONNECTED | 1.94
PETERSFIELD AVENUE PROJECT_564 | IVER 132KV |  |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 2
SLOUGH PROJECT_247 | IVER 132KV |  |  | OTHER SYNCHRONOUS | 33kV | CONNECTED | 60
SLOUGH PROJECT_260 | IVER 132KV |  |  | STEAM TURBINE | 33kV | ACCEPTED | 46
SUTTON LANE PROJECT_248 | IVER 132KV |  |  | CHP - GAS TURBINE | 11kV | CONNECTED | 4.5
SUTTON LANE PROJECT_249 | IVER 132KV |  |  | WASTE TO ENERGY | 11kV | CONNECTED | 1.5
SUTTON LANE PROJECT_250 | IVER 132KV |  |  | LANDFILL GAS | 11kV | CONNECTED | 2.8
UPTON PROJECT_253 | IVER 132KV |  |  | GAS TURBINE | 11kV | ACCEPTED | 0.4
ASHFORD COMMON PROJECT_263 | LALEHAM |  |  | DIESEL | 22kV | CONNECTED | 6
CAUSEWAY PROJECT_262 | LALEHAM |  |  | LANDFILL GAS | 11kV | CONNECTED | 3.5
CAUSEWAY PROJECT_266 | LALEHAM |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2.6
SIDNEY ROAD PROJECT_264 | LALEHAM |  |  | NATURAL GAS | 11kV | CONNECTED | 1.3
STAINES PROJECT_269 | LALEHAM |  |  | BATTERY | 33kV | ACCEPTED | 49
STAINES PROJECT_271 | LALEHAM |  |  | BATTERY | 33kV | ACCEPTED | 49
STAINES PROJECT_562 | LALEHAM |  |  | BATTERY | 33kV | ACCEPTED | 49.9
SUNBURY CROSS PROJECT_265 | LALEHAM |  |  | OTHER SYNCHRONOUS | 11kV | CONNECTED | 10
SUNBURY CROSS PROJECT_267 | LALEHAM |  |  | WASTE TO ENERGY | 11kV | ACCEPTED | 3.7
SUNBURY CROSS PROJECT_268 | LALEHAM |  |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 1.7
ASHLING ROAD PROJECT_296 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.1
ASHLING ROAD PROJECT_689 | LOVEDEAN |  |  | CHP - GAS TURBINE | 11kV | CONNECTED | 1.8
BILSHAM PROJECT_291 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 15
BILSHAM PROJECT_293 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3
BILSHAM PROJECT_294 | LOVEDEAN |  |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 0.772
BILSHAM PROJECT_302 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.2
BILSHAM PROJECT_708 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 15
BROCKHAMPTON PROJECT_276 | LOVEDEAN |  |  | CHP - GAS TURBINE | 11kV | CONNECTED | 3.3
BROCKHAMPTON PROJECT_282 | LOVEDEAN |  |  | NATURAL GAS | 11kV | CONNECTED | 5
BROCKHAMPTON PROJECT_314 | LOVEDEAN |  |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 5.32
BROCKHAMPTON PROJECT_667 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0
BROCKHAMPTON PROJECT_687 | LOVEDEAN |  |  | CHP - GAS TURBINE | 11kV | CONNECTED | 3
CHICHESTER & HUNSTON PROJECT_283 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
CHICHESTER & HUNSTON PROJECT_285 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6
CHICHESTER & HUNSTON PROJECT_290 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
CHICHESTER & HUNSTON PROJECT_292 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8
CHICHESTER & HUNSTON PROJECT_295 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8
CHICHESTER & HUNSTON PROJECT_298 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
CHICHESTER & HUNSTON PROJECT_301 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7
CHICHESTER & HUNSTON PROJECT_303 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4
CHICHESTER & HUNSTON PROJECT_308 | LOVEDEAN |  |  | PV & BATTERY | 33kV | CONNECTED | 7
CHICHESTER & HUNSTON PROJECT_581 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 15
CHICHESTER & HUNSTON PROJECT_677 | LOVEDEAN |  |  | BATTERY | 33kV | CONNECTED | 7
CHICHESTER PROJECT_272 | LOVEDEAN |  |  | NATURAL GAS | 11kV | CONNECTED | 8.6
CHICHESTER PROJECT_273 | LOVEDEAN |  |  | LANDFILL GAS | 11kV | CONNECTED | 3.75
CHICHESTER PROJECT_305 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
EMSWORTH PROJECT_665 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.8
EMSWORTH PROJECT_690 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.065
FAREHAM MAIN PROJECT_306 | LOVEDEAN |  |  | DIESEL | 33kV | CONNECTED | 20
FAREHAM MAIN PROJECT_313 | LOVEDEAN |  |  | BATTERY | 33kV | ACCEPTED | 40
FAREHAM MAIN PROJECT_699 | LOVEDEAN |  |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0
FAREHAM PROJECT_286 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 17.5
FAREHAM RESERVE PROJECT_668 | LOVEDEAN |  |  | CHP - GAS TURBINE | 33kV | ACCEPTED | 30.56
FRATTON PARK PROJECT_700 | LOVEDEAN |  |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0
GABLE HEAD PROJECT_711 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.24
GAMBLE ROAD PROJECT_666 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.8
GREETHAM STREET PROJECT_678 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.03
GREETHAM STREET PROJECT_679 | LOVEDEAN |  |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0.05
GREETHAM STREET PROJECT_702 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.12
HAVANT PROJECT_300 | LOVEDEAN |  |  | DIESEL | 33kV | CONNECTED | 20
HAVANT PROJECT_309 | LOVEDEAN |  |  | CHP - GAS TURBINE | 33kV | CONNECTED | 20
HILSEA INCINERATOR PROJECT_278 | LOVEDEAN |  |  | WASTE TO ENERGY | 33kV | CONNECTED | 20
HILSEA PROJECT_660 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.15
HILSEA PROJECT_683 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.108
HILSEA PROJECT_684 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.069
HOEFORD PROJECT_669 | LOVEDEAN |  |  | CHP - GAS TURBINE | 0.4kV | ACCEPTED | 0.5
HORNDEAN PROJECT_289 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
HORNDEAN PROJECT_709 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
HUNSTON PROJECT_281 | LOVEDEAN |  |  | DIESEL | 11kV | CONNECTED | 2
HUNSTON PROJECT_312 | LOVEDEAN |  |  | BATTERY | 11kV | ACCEPTED | 10
HUNSTON PROJECT_580 | LOVEDEAN |  |  | GAS TURBINE | 11kV | ACCEPTED | 6
HUNSTON PROJECT_688 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.035
HUNSTON PROJECT_694 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4
HUNSTON PROJECT_705 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.8
HUNSTON PROJECT_707 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.5
HUNTERS RACE PV PROJECT_287 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 9.45
LEIGH PARK PROJECT_277 | LOVEDEAN |  |  | LANDFILL GAS | 11kV | CONNECTED | 3.5
LEIGH PARK PROJECT_697 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.243
MANOR FARM SHRIPNEY PV GENERATION PROJECT_299 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8
PLESSEY, TITCHFIELD PROJECT_284 | LOVEDEAN |  |  | DIESEL | 33kV | CONNECTED | 24
PORTCHESTER PROJECT_279 | LOVEDEAN |  |  | LANDFILL GAS | 11kV | CONNECTED | 3.5
PORTSMOUTH PROJECT_288 | LOVEDEAN |  |  | OTHER SYNCHRONOUS | 33kV | CONNECTED | 1
PORTSMOUTH PROJECT_675 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.25
PORTSMOUTH PROJECT_680 | LOVEDEAN |  |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0.015
PORTSMOUTH PROJECT_701 | LOVEDEAN |  |  | CHP - GAS TURBINE | 33kV | CONNECTED | 0
ROSE GREEN PROJECT_274 | LOVEDEAN |  |  | DIESEL | 11kV | CONNECTED | 5
ROSE GREEN PROJECT_275 | LOVEDEAN |  |  | LANDFILL GAS | 11kV | CONNECTED | 3.045
SOUTH BERSTED PROJECT_672 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0
SOUTH BERSTED PROJECT_696 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.313
SOUTHWICK ESTATE PV PROJECT_297 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 40
TITCHFIELD PROJECT_698 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.15
TITCHFIELD PROJECT_712 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.171
WATERLOOVILLE PROJECT_681 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.05
WYMERING & FORT WIDLEY PROJECT_307 | LOVEDEAN |  |  | DIESEL | 33kV | CONNECTED | 19.85
WYMERING & FORT WIDLEY PROJECT_310 | LOVEDEAN |  |  | LANDFILL GAS | 33kV | ACCEPTED | 20
WYMERING PROJECT_280 | LOVEDEAN |  |  | CHP - GAS TURBINE | 11kV | CONNECTED | 4
WYMERING PROJECT_673 | LOVEDEAN |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0
WYMERING PROJECT_674 | LOVEDEAN |  |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0.135
ALDERNEY PROJECT_315 | MANNINGTON GSP |  |  | LANDFILL GAS | 11kV | CONNECTED | 7.5
ALDERNEY PROJECT_316 | MANNINGTON GSP |  |  | NATURAL GAS | 11kV | CONNECTED | 1.4
BLANDFORD PROJECT_397 | MANNINGTON GSP |  |  | GAS | 11kV | ACCEPTED | 0
BLANDFORD PROJECT_398 | MANNINGTON GSP |  |  | DIESEL | 11kV | ACCEPTED | 0
BOURTON PROJECT_335 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.5
BOVINGTON PROJECT_396 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
CENTRAL PROJECT_331 | MANNINGTON GSP |  |  | CHP - GAS TURBINE | 11kV | DISCONNECTED | 5.4
CHRISTCHURCH PROJECT_330 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7.5
CHRISTCHURCH PROJECT_355 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
CHRISTCHURCH PROJECT_368 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 3
CORFE MULLEN PROJECT_317 | MANNINGTON GSP |  |  | LANDFILL GAS | 11kV | CONNECTED | 1.15
CREEKMOOR PROJECT_359 | MANNINGTON GSP |  |  | WASTE TO ENERGY | 11kV | CONNECTED | 1.024
ELECTRIC HOUSE PROJECT_374 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.25
HOLES BAY PROJECT_373 | MANNINGTON GSP |  |  | BATTERY | 11kV | ACCEPTED | 7.5
HOLES BAY PROJECT_385 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.37
LYMINGTON PROJECT_361 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2
LYMINGTON PROJECT_372 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.17
LYTCHETT PROJECT_338 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 3.3
LYTCHETT PROJECT_339 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7.2
LYTCHETT PROJECT_340 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
LYTCHETT PROJECT_343 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12.8
LYTCHETT PROJECT_346 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 9.36
LYTCHETT PROJECT_360 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
LYTCHETT PROJECT_395 | MANNINGTON GSP |  |  | BATTERY | 33kV | ACCEPTED | 25
LYTCHETT PROJECT_583 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 12
MANNINGTON GSP PROJECT_322 | MANNINGTON GSP |  |  | NATURAL GAS | 132kV | CONNECTED | 9.5
MANNINGTON GSP PROJECT_389 | MANNINGTON GSP |  |  | BATTERY | 132kV | ACCEPTED | 49.5
MANNINGTON GSP PROJECT_391 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT + BATTERY STORAGE | 132kV | ACCEPTED | 40
MANNINGTON GSP PROJECT_574 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 49.99
MANNINGTON GSP PROJECT_575 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 29.4
MANNINGTON PROJECT_319 | MANNINGTON GSP |  |  | LANDFILL GAS | 33kV | CONNECTED | 3.16
MANNINGTON PROJECT_341 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.025
MANNINGTON PROJECT_342 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 11.2
MANNINGTON PROJECT_347 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 11
MANNINGTON PROJECT_348 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 16
MANNINGTON PROJECT_356 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.032
MANNINGTON PROJECT_386 | MANNINGTON GSP |  |  | BATTERY | 33kV | ACCEPTED | 49.9
MANNINGTON PROJECT_393 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT + BATTERY STORAGE | 33kV | ACCEPTED | 8
MILL LANE PROJECT_318 | MANNINGTON GSP |  |  | LANDFILL GAS | 11kV | CONNECTED | 1
MILL LANE PROJECT_571 | MANNINGTON GSP |  |  | LANDFILL GAS | 11kV | ACCEPTED | 7.6
NEW MILTON PROJECT_332 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.7
NEW MILTON PROJECT_378 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.05
POOLE (HILL STREET) PROJECT_379 | MANNINGTON GSP |  |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 0
POOLE (HILL STREET) PROJECT_390 | MANNINGTON GSP |  |  | DIESEL | 11kV | ACCEPTED | 3.4
REDHILL PROJECT_324 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 20.31
REDHILL PROJECT_352 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 24.8
REDHILL PROJECT_353 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5.9
REDHILL PROJECT_354 | MANNINGTON GSP |  |  | ANAEROBIC DIGESTER | 33kV | ACCEPTED | 5
REDHILL PROJECT_363 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 3.5
REDHILL PROJECT_364 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.9
REDHILL PROJECT_365 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3.81
REDHILL PROJECT_387 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 3.7
REDLYNCH PROJECT_327 | MANNINGTON GSP |  |  | LANDFILL GAS | 11kV | CONNECTED | 0.6
REDLYNCH PROJECT_328 | MANNINGTON GSP |  |  | LANDFILL GAS | 11kV | CONNECTED | 1
REDLYNCH PROJECT_337 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 6
SALISBURY PROJECT_325 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 9.25
SALISBURY PROJECT_572 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 12.5
SHAFTESBURY PROJECT_323 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8.6
SHAFTESBURY PROJECT_326 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12
SHAFTESBURY PROJECT_349 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.5
SHAFTESBURY PROJECT_357 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.5
SHAFTESBURY PROJECT_358 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4
SHAFTESBURY PROJECT_366 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.5
SHAFTESBURY PROJECT_367 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 4.125
SHAFTESBURY PROJECT_370 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.08
SHAFTESBURY PROJECT_377 | MANNINGTON GSP |  |  | BATTERY | 33kV | ACCEPTED | 20
SHAFTESBURY PROJECT_384 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.237
SHAFTESBURY PROJECT_392 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 11
SHROTON PROJECT_334 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 6.6
SOMERFORD PROJECT_375 | MANNINGTON GSP |  |  | OTHER SYNCHRONOUS | 11kV | CONNECTED | 1
VERWOOD PROJECT_394 | MANNINGTON GSP |  |  | GAS | 11kV | ACCEPTED | 5
WAREHAM PROJECT_321 | MANNINGTON GSP |  |  | LANDFILL GAS | 33kV | CONNECTED | 3.23
WAREHAM PROJECT_329 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6
WAREHAM PROJECT_345 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 9
WAREHAM PROJECT_350 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 3.96
WAREHAM PROJECT_351 | MANNINGTON GSP |  |  | LANDFILL GAS | 33kV | ACCEPTED | 20.8
WAREHAM PROJECT_573 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 0
WAREHAM TOWN PROJECT_376 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.1
WINCANTON PROJECT_336 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
WINTON PROJECT_320 | MANNINGTON GSP |  |  | DIESEL | 11kV | CONNECTED | 5.061
ANDOVER PROJECT_52 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
ANDOVER PROJECT_53 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 14.31
ANDOVER PROJECT_59 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 39.3
ANDOVER PROJECT_60 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 3.5
ASHTON PARK PROJECT_443 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
ASHTON PARK PROJECT_713 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.175
AVON RUBBER PROJECT_458 | MELKSHAM |  |  | PV AND BATTERY | 11kV | ACCEPTED | 0.14
BRADFORD-ON-AVON PROJECT_597 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.125
BROMHAM PROJECT_452 | MELKSHAM |  |  | GAS TURBINE | 11kV | CONNECTED | 0.4
BRUTON PROJECT_449 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.202
CALNE PROJECT_405 | MELKSHAM |  |  | LANDFILL GAS | 11kV | CONNECTED | 2.5
CALNE PROJECT_406 | MELKSHAM |  |  | LANDFILL GAS | 11kV | CONNECTED | 2.5
CALNE PROJECT_461 | MELKSHAM |  |  | GAS TURBINE | 11kV | ACCEPTED | 7.5
CHIPPENHAM PROJECT_399 | MELKSHAM |  |  | NATURAL GAS | 33kV | CONNECTED | 12
CHIPPENHAM PROJECT_401 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
CHIPPENHAM PROJECT_402 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.5
CHIPPENHAM PROJECT_408 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6.5
CHIPPENHAM PROJECT_409 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12
CHIPPENHAM PROJECT_414 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6.1
CHIPPENHAM PROJECT_421 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 11
CHIPPENHAM PROJECT_422 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7
CHIPPENHAM PROJECT_426 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12
CHIPPENHAM PROJECT_464 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 40
CHIPPENHAM PROJECT_584 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 42
CHIPPENHAM PROJECT_595 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 42.11
CODFORD PROJECT_418 | MELKSHAM |  |  | ANAEROBIC DIGESTER | 11kV | CONNECTED | 2
CORSHAM PROJECT_416 | MELKSHAM |  |  | OTHER SYNCHRONOUS | 11kV | CONNECTED | 2
CROCKERTON PROJECT_415 | MELKSHAM |  |  | STEAM TURBINE | 11kV | CONNECTED | 1
DEVIZES PROJECT_429 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.3
DEVIZES PROJECT_598 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.068
FROME PROJECT_ | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 10.53
FROME PROJECT_413 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 9.5
FROME PROJECT_420 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8
FROME PROJECT_423 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6.5
FROME PROJECT_433 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
FROME PROJECT_434 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7
FROME PROJECT_435 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12.16
FROME PROJECT_442 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
FROME PROJECT_448 | MELKSHAM |  |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0.05
FROME PROJECT_456 | MELKSHAM |  |  | BATTERY | 33kV | ACCEPTED | 0.8
FROME PROJECT_457 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6.35
FROME PROJECT_459 | MELKSHAM |  |  | WASTE TO ENERGY | 33kV | ACCEPTED | 26.5
FROME PROJECT_460 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4
FROME PROJECT_465 | MELKSHAM |  |  | BATTERY | 33kV | ACCEPTED | 7
FROME PROJECT_594 | MELKSHAM |  |  | GAS TURBINE | 11kV | ACCEPTED | 2.67
HAWKERIDGE PROJECT_450 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.08
HAWKERIDGE PROJECT_451 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.1
HAWKERIDGE PROJECT_578 | MELKSHAM |  |  | NATURAL GAS | 11kV | ACCEPTED | 7.56
HAWKERIDGE PROJECT_593 | MELKSHAM |  |  | GAS TURBINE | 11kV | ACCEPTED | 7.6
HOLWELL PROJECT_436 | MELKSHAM |  |  | WIND FARM | 11kV | CONNECTED | 0.5
HOLWELL PROJECT_437 | MELKSHAM |  |  | WIND FARM | 11kV | CONNECTED | 0.5
LYNEHAM PROJECT_407 | MELKSHAM |  |  | DIESEL | 11kV | CONNECTED | 2.75
MALMESBURY PROJECT_455 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.5
MELKSHAM PROJECT_439 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 132kV | CONNECTED | 41.2
MELKSHAM PROJECT_453 | MELKSHAM |  |  | BATTERY | 132kV | ACCEPTED | 105.2
MELKSHAM PROJECT_463 | MELKSHAM |  |  | PV AND BATTERY | 132kV | ACCEPTED | 49.9
MELKSHAM TOWN PROJECT_417 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.5
MELKSHAM TOWN PROJECT_468 | MELKSHAM |  |  | GAS TURBINE | 11kV | ACCEPTED | 7.2
MIDDLE WALLOP PROJECT_55 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.4
MIDDLE WALLOP PROJECT_61 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.4
NORRINGTON PROJECT_400 | MELKSHAM |  |  | NATURAL GAS | 33kV | CONNECTED | 5.45
NORRINGTON PROJECT_403 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.5
NORRINGTON PROJECT_419 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
NORRINGTON PROJECT_424 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.5
NORRINGTON PROJECT_425 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 14
NORRINGTON PROJECT_428 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12.16
NORRINGTON PROJECT_430 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
NORRINGTON PROJECT_431 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 13
NORRINGTON PROJECT_432 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
NORRINGTON PROJECT_438 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 20
NORRINGTON PROJECT_440 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.4
NORRINGTON PROJECT_447 | MELKSHAM |  |  | CHP - GAS TURBINE | 33kV | CONNECTED | 0.5
NORRINGTON PROJECT_466 | MELKSHAM |  |  | BATTERY | 33kV | ACCEPTED | 20
NORRINGTON PROJECT_469 | MELKSHAM |  |  | NATURAL GAS | 33kV | CONNECTED | 16
NORRINGTON PROJECT_579 | MELKSHAM |  |  | PV & BATTERY | 33kV | ACCEPTED | 20
PORTWAY PROJECT_51 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 6.3
PORTWAY PROJECT_64 | MELKSHAM |  |  | DIESEL | 11kV | CONNECTED | 1.76
SPRING QUARRY WEST PROJECT_445 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 7
SPRING QUARRY WEST PROJECT_467 | MELKSHAM |  |  | GAS TURBINE | 11kV | ACCEPTED | 5
SUTTON BENGER PROJECT_589 | MELKSHAM |  |  | BATTERY | 11kV | ACCEPTED | 0.914
TROWBRIDGE TOWN PROJECT_444 | MELKSHAM |  |  | DIESEL | 11kV | CONNECTED | 2.5
WEST GRAFTON PROJECT_411 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5.64
WEST GRAFTON VILLAGE PROJECT_427 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.18
WESTBURY PROJECT_404 | MELKSHAM |  |  | LANDFILL GAS | 11kV | CONNECTED | 4.76
CIRENCESTER PROJECT_480 | MINETY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
CIRENCESTER PROJECT_481 | MINETY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7
CIRENCESTER PROJECT_482 | MINETY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8.7
CIRENCESTER PROJECT_515 | MINETY |  |  | BATTERY | 33kV | ACCEPTED | 10
CIRENCESTER PROJECT_523 | MINETY |  |  | PV AND BATTERY | 33kV | ACCEPTED | 10
CIRENCESTER PROJECT_524 | MINETY |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 75
CIRENCESTER PROJECT_588 | MINETY |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 10
CIRENCESTER PROJECT_658 | MINETY |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 24.2
CIRENCESTER TOWN PROJECT_505 | MINETY |  |  | PV & BATTERY | 11kV | ACCEPTED | 1
GALILEO PROJECT_511 | MINETY |  |  | BATTERY | 11kV | ACCEPTED | 10
HONDA PROJECT_476 | MINETY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 17.9
MINETY PROJECT_496 | MINETY |  |  | PHOTOVOLTAIC PLANT | 132kV | CONNECTED | 49.9
MINETY PROJECT_499 | MINETY |  |  | BATTERY | 132kV | ACCEPTED | 105.2
MINETY PROJECT_506 | MINETY |  |  | BATTERY | 132kV | ACCEPTED | 157.58
MINETY PROJECT_510 | MINETY |  |  | BATTERY | 132kV | ACCEPTED | 49.9
MINETY PROJECT_518 | MINETY |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 50
PARK NORTH PROJECT_519 | MINETY |  |  | CHP - SPARK IGNITION | 11kV | ACCEPTED | 1
QUARRY ROAD PROJECT_509 | MINETY |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 1.8
STANTON FITZWARREN PROJECT_491 | MINETY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
STANTON FITZWARREN PROJECT_492 | MINETY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3.5
STRATTON MAIN PROJECT_487 | MINETY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 28.6
STRATTON MAIN PROJECT_488 | MINETY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 22.6
STRATTON MAIN PROJECT_503 | MINETY |  |  | BATTERY | 33kV | ACCEPTED | 20
STRATTON PROJECT_497 | MINETY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.71
STRATTON PROJECT_498 | MINETY |  |  | DIESEL | 11kV | CONNECTED | 2
STRATTON PROJECT_514 | MINETY |  |  | BATTERY | 11kV | ACCEPTED | 1.36
STRATTON PROJECT_590 | MINETY |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.526
STRATTON RESERVE PROJECT_471 | MINETY |  |  | WIND FARM | 33kV | CONNECTED | 6.5
STRATTON RESERVE PROJECT_477 | MINETY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
STRATTON RESERVE PROJECT_478 | MINETY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
STRATTON RESERVE PROJECT_486 | MINETY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 9
SWINDON PROJECT_ | MINETY |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 24.53
SWINDON PROJECT_470 | MINETY |  |  | LANDFILL GAS | 33kV | CONNECTED | 4.64
SWINDON PROJECT_479 | MINETY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
SWINDON PROJECT_484 | MINETY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8
SWINDON PROJECT_485 | MINETY |  |  | DIESEL | 11kV | CONNECTED | 1.781
SWINDON PROJECT_493 | MINETY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
SWINDON PROJECT_494 | MINETY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
SWINDON PROJECT_502 | MINETY |  |  | DIESEL | 33kV | CONNECTED | 6
SWINDON PROJECT_507 | MINETY |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 2.5
SWINDON PROJECT_512 | MINETY |  |  | BATTERY | 11kV | ACCEPTED | 1.2
SWINDON PROJECT_516 | MINETY |  |  | BATTERY | 33kV | ACCEPTED | 1.5
SWINDON PROJECT_517 | MINETY |  |  | BATTERY | 33kV | ACCEPTED | 12
SWINDON PROJECT_657 | MINETY |  |  | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.163
TOOTHILL PROJECT_472 | MINETY |  |  | LANDFILL GAS | 11kV | CONNECTED | 2
TOOTHILL PROJECT_489 | MINETY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 48.51
TOOTHILL PROJECT_490 | MINETY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8.2
TOOTHILL PROJECT_495 | MINETY |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6.76
TOOTHILL PROJECT_508 | MINETY |  |  | BATTERY | 33kV | ACCEPTED | 30
TOOTHILL PROJECT_656 | MINETY |  |  | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.058
TRADING ESTATE PROJECT_473 | MINETY |  |  | DIESEL | 11kV | CONNECTED | 0.42
TRADING ESTATE PROJECT_504 | MINETY |  |  | CHP - SPARK IGNITION | 11kV | CONNECTED | 2.15
WOOTTON BASSETT PROJECT_474 | MINETY |  |  | WASTE TO ENERGY | 11kV | CONNECTED | 2
WOOTTON BASSETT PROJECT_475 | MINETY |  |  | LANDFILL GAS | 11kV | CONNECTED | 2
WOOTTON BASSETT PROJECT_483 | MINETY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
WOOTTON BASSETT PROJECT_522 | MINETY |  |  | LANDFILL GAS | 11kV | ACCEPTED | 6.5
WOOTTON BASSETT PROJECT_659 | MINETY |  |  | GAS TURBINE | 11kV | ACCEPTED | 7.5
WROUGHTON PROJECT_500 | MINETY |  |  | LANDFILL GAS | 11kV | CONNECTED | 2
WROUGHTON PROJECT_501 | MINETY |  |  | LANDFILL GAS | 11kV | CONNECTED | 2
WROUGHTON PROJECT_513 | MINETY |  |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 7
BASSETT PROJECT_719 | NURSLING |  |  | LANDFILL GAS | 11kV | ACCEPTED | 0.21
BASSETT PROJECT_728 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.021
BEVOIS VALLEY PROJECT_532 | NURSLING |  |  | CHP - GAS TURBINE | 6.6kV | CONNECTED | 1
BEVOIS VALLEY PROJECT_722 | NURSLING |  |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0.175
DUNBRIDGE PROJECT_591 | NURSLING |  |  | PV & BATTERY | 0.4kV | ACCEPTED | 0.044
EASTLEIGH NORTH PROJECT_528 | NURSLING |  |  | LANDFILL GAS | 11kV | CONNECTED | 2.92
EASTLEIGH NORTH PROJECT_542 | NURSLING |  |  | OTHER SYNCHRONOUS | 0.4kV | CONNECTED | 1
HARESTOCK PROJECT_716 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.42
HARESTOCK PROJECT_726 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.05
MARCHWOOD PROJECT_527 | NURSLING |  |  | WASTE TO ENERGY | 11kV | CONNECTED | 17.5
MARCHWOOD PROJECT_533 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
MAYBUSH PROJECT_526 | NURSLING |  |  | NATURAL GAS | 11kV | CONNECTED | 2
NURSLING PROJECT_534 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 132kV | CONNECTED | 50
NURSLING PROJECT_536 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 40
REGENTS PARK PROJECT_530 | NURSLING |  |  | WASTE TO ENERGY | 11kV | CONNECTED | 1.2
ROWNHAMS PROJECT_535 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
ROWNHAMS PROJECT_537 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.32
ROWNHAMS PROJECT_538 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.99
ROWNHAMS PROJECT_540 | NURSLING |  |  | BATTERY | 33kV | ACCEPTED | 10
ROWNHAMS PROJECT_544 | NURSLING |  |  | BATTERY | 33kV | ACCEPTED | 10
ROWNHAMS PROJECT_545 | NURSLING |  |  | OTHER SYNCHRONOUS | 33kV | ACCEPTED | 20
ROWNHAMS PROJECT_550 | NURSLING |  |  | NATURAL GAS | 33kV | ACCEPTED | 20
ROWNHAMS PROJECT_551 | NURSLING |  |  | NATURAL GAS | 33kV | CONNECTED | 20
SILKSTEAD PROJECT_548 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.5
SILKSTEAD PROJECT_717 | NURSLING |  |  | OTHER SYNCHRONOUS | 11kV | ACCEPTED | 0.37
SILKSTEAD PROJECT_720 | NURSLING |  |  | OTHER SYNCHRONOUS | 11kV | ACCEPTED | 0.2
SOUTHAMPTON RESERVE PROJECT_525 | NURSLING |  |  | GEOTHERMAL | 33kV | CONNECTED | 7
SOUTHAMPTON RESERVE PROJECT_546 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 0.81
SOUTHAMPTON RESERVE PROJECT_714 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 1.9
SOUTHAMPTON RESERVE PROJECT_723 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0
SOUTHAMPTON RESERVE PROJECT_727 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.037
SOUTHAMPTON RESERVE PROJECT_729 | NURSLING |  |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 0.015
ST CROSS PROJECT_724 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.064
TOTTON PROJECT_549 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2
VELMORE PROJECT_529 | NURSLING |  |  | DIESEL | 11kV | CONNECTED | 1.5
VELMORE PROJECT_531 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6.3
VELMORE PROJECT_539 | NURSLING |  |  | DIESEL | 33kV | ACCEPTED | 20
WESTERN ESPLANADE PROJECT_682 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.18
WESTERN ESPLANADE PROJECT_721 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.18
WINCHESTER PROJECT_541 | NURSLING |  |  | OTHER SYNCHRONOUS | 33kV | ACCEPTED | 20
WINCHESTER PROJECT_577 | NURSLING |  |  | BATTERY | 33kV | ACCEPTED | 10
GREENFORD PROJECT_556 | WILLESDEN |  |  | NATURAL GAS | 11kV | CONNECTED | 1
FLACKWELL HEATH PROJECT_1 |  | LOUDWATER |  | LANDFILL GAS | 11kV | CONNECTED | 1.4
LOUDWATER PROJECT_2 |  | LOUDWATER |  | BATTERY | 33kV | ACCEPTED | 40
WELL END PROJECT_3 |  | LOUDWATER |  | BATTERY | 11kV | ACCEPTED | 7.2
CASTLE CARY PROJECT_12 |  | YEOVIL |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.32
CASTLE CARY PROJECT_4 |  | YEOVIL |  | LANDFILL GAS | 11kV | CONNECTED | 3.8
CHILTON CANTELLO PROJECT_5 |  | YEOVIL |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
HENSTRIDGE PROJECT_11 |  | YEOVIL |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.13
HENSTRIDGE PROJECT_13 |  | YEOVIL |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.1
MILBORNE PORT PROJECT_20 |  | YEOVIL |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
SPARKFORD PROJECT_14 |  | YEOVIL |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.2
YEOVIL PROJECT_10 |  | YEOVIL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.13
YEOVIL PROJECT_21 |  | YEOVIL |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 9
YEOVIL PROJECT_22 |  | YEOVIL |  | CHP - GAS TURBINE | 33kV | ACCEPTED | 15
YEOVIL PROJECT_23 |  | YEOVIL |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 7.6
YEOVIL PROJECT_24 |  | YEOVIL |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 10
YEOVIL PROJECT_6 |  | YEOVIL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10.59
YEOVIL PROJECT_7 |  | YEOVIL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8.8
YEOVIL PROJECT_8 |  | YEOVIL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5.55
YEOVIL PROJECT_9 |  | YEOVIL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7.5
YETMINSTER PROJECT_15 |  | YEOVIL |  | DIESEL | 11kV | CONNECTED | 0.4
YETMINSTER PROJECT_16 |  | YEOVIL |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0.25
YETMINSTER PROJECT_17 |  | YEOVIL |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.15
BOTLEY WOOD PROJECT_29 |  | BOTLEY WOOD |  | LANDFILL GAS | 33kV | ACCEPTED | 14
BOTLEY WOOD PROJECT_30 |  | BOTLEY WOOD |  | DIESEL | 33kV | CONNECTED | 20
BOTLEY WOOD PROJECT_558 |  | BOTLEY WOOD |  | BATTERY | 33kV | ACCEPTED | 49.9
BISHOPS WALTHAM PROJECT_27 |  | NETLEY COMMON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
BISHOPS WALTHAM PROJECT_686 |  | NETLEY COMMON |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 2.5
HAMBLE PROJECT_33 |  | NETLEY COMMON |  | BATTERY | 11kV | ACCEPTED | 5
HAMBLE PROJECT_585 |  | NETLEY COMMON |  | LANDFILL GAS | 11kV | ACCEPTED | 7.2
NETLEY COMMON PROJECT_28 |  | NETLEY COMMON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12
NETLEY COMMON PROJECT_31 |  | NETLEY COMMON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
WESTON PROJECT_26 |  | NETLEY COMMON |  | LANDFILL GAS | 11kV | CONNECTED | 2.6
AMESBURY PROJECT_410 |  | AMESBURY |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5.64
AMESBURY PROJECT_412 |  | AMESBURY |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.6
AMESBURY PROJECT_446 |  | AMESBURY |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 3.5
BOSCOMBE DOWN PROJECT_441 |  | AMESBURY |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 10
BOSCOMBE DOWN PROJECT_454 |  | AMESBURY |  | DIESEL | 11kV | CONNECTED | 4
BEENHAM PROJECT_54 |  | THATCHAM |  | LANDFILL GAS | 11kV | CONNECTED | 1.9
KINTBURY PROJECT_56 |  | THATCHAM |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.2
TADLEY PROJECT_62 |  | THATCHAM |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.3
THATCHAM PROJECT_49 |  | THATCHAM |  | NATURAL GAS | 11kV | CONNECTED | 9.6
THATCHAM PROJECT_50 |  | THATCHAM |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.7
THATCHAM PROJECT_57 |  | THATCHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 14
THATCHAM PROJECT_58 |  | THATCHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 16
THATCHAM PROJECT_65 |  | THATCHAM |  | GAS TURBINE | 33kV | ACCEPTED | 20.53
BASINGSTOKE PROJECT_36 |  | BASINGSTOKE T1A & T2A |  | WASTE TO ENERGY | 11kV | CONNECTED | 12
BASINGSTOKE PROJECT_37 |  | BASINGSTOKE T1A & T2A |  | OTHER SYNCHRONOUS | 11kV | CONNECTED | 0.75
BASINGSTOKE T1A & T2A PROJECT_41 |  | BASINGSTOKE T1A & T2A |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4
BASINGSTOKE T1A & T2A PROJECT_42 |  | BASINGSTOKE T1A & T2A |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 3
BASINGSTOKE T1A & T2A PROJECT_559 |  | BASINGSTOKE T1A & T2A |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 14.2
JAYS CLOSE PROJECT_46 |  | BASINGSTOKE T1A & T2A |  | DIESEL | 11kV | CONNECTED | 4
ARBORFIELD PROJECT_34 |  | BASINGSTOKE T1B & T2B |  | LANDFILL GAS | 11kV | CONNECTED | 1
ARBORFIELD PROJECT_35 |  | BASINGSTOKE T1B & T2B |  | OTHER SYNCHRONOUS | 11kV | CONNECTED | 1.44
BASINGSTOKE T1B & T2B PROJECT_44 |  | BASINGSTOKE T1B & T2B |  | GAS TURBINE | 33kV | CONNECTED | 16
BASINGSTOKE T1B & T2B PROJECT_603 |  | BASINGSTOKE T1B & T2B |  | BATTERY | 33kV | ACCEPTED | 25
CHINEHAM PROJECT_45 |  | BASINGSTOKE T1B & T2B |  | CHP - GAS TURBINE | 11kV | CONNECTED | 1.368
OVERTON PROJECT_39 |  | BASINGSTOKE T1B & T2B |  | NATURAL GAS | 11kV | CONNECTED | 7.2
OVERTON PROJECT_43 |  | BASINGSTOKE T1B & T2B |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3.2
OVERTON PROJECT_605 |  | BASINGSTOKE T1B & T2B |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 1.2
BASINGSTOKE T3 & T4 PROJECT_47 |  | BASINGSTOKE T3 & T4 |  | BATTERY | 33kV | ACCEPTED | 20
BASINGSTOKE T3 & T4 PROJECT_654 |  | BASINGSTOKE T3 & T4 |  | PV & BATTERY | 33kV | ACCEPTED | 31.58
HOUNDMILLS PROJECT_38 |  | BASINGSTOKE T3 & T4 |  | NATURAL GAS | 11kV | CONNECTED | 1.3
HOUNDMILLS PROJECT_40 |  | BASINGSTOKE T3 & T4 |  | DIESEL | 11kV | CONNECTED | 1.2
CHICKERELL PROJECT_661 |  | CHICKERELL |  | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.069
CHICKERELL PROJECT_67 |  | CHICKERELL |  | NATURAL GAS | 33kV | CONNECTED | 47.8
CHICKERELL PROJECT_670 |  | CHICKERELL |  | WASTE TO ENERGY | 33kV | ACCEPTED | 15.2
CHICKERELL PROJECT_692 |  | CHICKERELL |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.7
CHICKERELL PROJECT_695 |  | CHICKERELL |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2.2
CHICKERELL PROJECT_72 |  | CHICKERELL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7.2
CHICKERELL PROJECT_73 |  | CHICKERELL |  | ANAEROBIC DIGESTER | 33kV | CONNECTED | 1.3
CHICKERELL PROJECT_76 |  | CHICKERELL |  | BATTERY | 33kV | ACCEPTED | 10
CHICKERELL PROJECT_77 |  | CHICKERELL |  | BATTERY | 33kV | ACCEPTED | 5
DORCHESTER PROJECT_671 |  | CHICKERELL |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 0
DORCHESTER PROJECT_68 |  | CHICKERELL |  | NATURAL GAS | 11kV | CONNECTED | 1.44
DORCHESTER PROJECT_710 |  | CHICKERELL |  | ANAEROBIC DIGESTER | 11kV | CONNECTED | 0.36
DORCHESTER PROJECT_74 |  | CHICKERELL |  | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.095
DORCHESTER PROJECT_75 |  | CHICKERELL |  | CHP - GAS TURBINE | 0.4kV | ACCEPTED | 0.1
PORTLAND PROJECT_69 |  | CHICKERELL |  | DIESEL | 11kV | CONNECTED | 2.4
WEYMOUTH PROJECT_70 |  | CHICKERELL |  | NATURAL GAS | 11kV | CONNECTED | 3.02
WINTERBOURNE KINGSTON PROJECT_371 |  | CHICKERELL |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.124
COWLEY LOCAL MAIN PROJECT_129 |  | COWLEY LOCAL MAIN |  | BATTERY | 33kV | ACCEPTED | 11
COWLEY LOCAL PROJECT_118 |  | COWLEY LOCAL MAIN |  | DIESEL | 11kV | CONNECTED | 0.56
COWLEY LOCAL PROJECT_620 |  | COWLEY LOCAL MAIN |  | OTHER SYNCHRONOUS | 11kV | CONNECTED | 0.149
ROSE HILL PROJECT_641 |  | COWLEY LOCAL MAIN |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0.8
BERINSFIELD PROJECT_100 |  | COWLEY LOCAL RESERVE |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2
BERINSFIELD PROJECT_109 |  | COWLEY LOCAL RESERVE |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.14
COWLEY LOCAL RESERVE PROJECT_586 |  | COWLEY LOCAL RESERVE |  | PV & BATTERY | 33kV | ACCEPTED | 50
COWLEY LOCAL RESERVE PROJECT_98 |  | COWLEY LOCAL RESERVE |  | GAS TURBINE | 33kV | CONNECTED | 12
KENNINGTON PROJECT_622 |  | COWLEY LOCAL RESERVE |  | SMALL HYDRO | 11kV | CONNECTED | 0.4
WALLINGFORD PROJECT_121 |  | COWLEY LOCAL RESERVE |  | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.05
WALLINGFORD PROJECT_610 |  | COWLEY LOCAL RESERVE |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.684
WALLINGFORD PROJECT_614 |  | COWLEY LOCAL RESERVE |  | LANDFILL GAS | 11kV | CONNECTED | 2.4
WALLINGFORD PROJECT_99 |  | COWLEY LOCAL RESERVE |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.36
CHOLSEY PROJECT_619 |  | DRAYTON |  | LANDFILL GAS | 11kV | CONNECTED | 0.05
CHOLSEY PROJECT_623 |  | DRAYTON |  | LANDFILL GAS | 11kV | CONNECTED | 0.25
DRAYTON PROJECT_1 |  | DRAYTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 20
DRAYTON PROJECT_101 |  | DRAYTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 21.25
DRAYTON PROJECT_125 |  | DRAYTON |  | GAS TURBINE | 33kV | ACCEPTED | 13
DRAYTON PROJECT_2 |  | DRAYTON |  | GAS TURBINE | 33kV | ACCEPTED | 18
DRAYTON PROJECT_86 |  | DRAYTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
DRAYTON PROJECT_89 |  | DRAYTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 14.1
DRAYTON PROJECT_95 |  | DRAYTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 35
DRAYTON PROJECT_96 |  | DRAYTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12.2
FULSCOT PROJECT_131 |  | DRAYTON |  | LANDFILL GAS | 11kV | ACCEPTED | 7.56
MILTON PROJECT_612 |  | DRAYTON |  | LANDFILL GAS | 11kV | CONNECTED | 0.45
MILTON PROJECT_626 |  | DRAYTON |  | SMALL HYDRO | 11kV | CONNECTED | 0.406
MILTON PROJECT_645 |  | DRAYTON |  | DIESEL | 11kV | CONNECTED | 1
MILTON PROJECT_649 |  | DRAYTON |  | DIESEL | 11kV | ACCEPTED | 0.001
MILTON PROJECT_81 |  | DRAYTON |  | DIESEL | 11kV | CONNECTED | 3.3
MILTON PROJECT_91 |  | DRAYTON |  | OTHER SYNCHRONOUS | 11kV | CONNECTED | 1.68
WANTAGE PROJECT_616 |  | DRAYTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.05
WINSMORE LANE PROJECT_647 |  | DRAYTON |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.001
ARNCOTT PROJECT_102 |  | HEADINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7.2
ARNCOTT PROJECT_124 |  | HEADINGTON |  | GAS TURBINE | 11kV | ACCEPTED | 5
HEADINGTON PROJECT_103 |  | HEADINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12
HEADINGTON PROJECT_132 |  | HEADINGTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 13
HEADINGTON PROJECT_141 |  | HEADINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
HEADINGTON PROJECT_582 |  | HEADINGTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 18
HEADINGTON PROJECT_93 |  | HEADINGTON |  | CHP - GAS TURBINE | 11kV | CONNECTED | 3.6
HEADINGTON PROJECT_94 |  | HEADINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
OLD ROAD PROJECT_635 |  | HEADINGTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.344
WHEATLEY PROJECT_570 |  | HEADINGTON |  | NATURAL GAS | 11kV | ACCEPTED | 7.12
HIGH WYCOMBE PROJECT_628 |  | HIGH WYCOMBE |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0.07
HIGH WYCOMBE PROJECT_84 |  | HIGH WYCOMBE |  | LANDFILL GAS | 11kV | CONNECTED | 1
WATLINGTON PROJECT_104 |  | HIGH WYCOMBE |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 17
NORTH HINKSEY PROJECT_618 |  | OXFORD |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.3
OSNEY PROJECT_636 |  | OXFORD |  | DIESEL | 11kV | CONNECTED | 0.504
OXFORD PROJECT_634 |  | OXFORD |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.21
OXFORD PROJECT_642 |  | OXFORD |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.2
OXFORD PROJECT_643 |  | OXFORD |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0.02
ST EBBES PROJECT_631 |  | OXFORD |  | DIESEL | 11kV | CONNECTED | 0.2
ST EBBES PROJECT_632 |  | OXFORD |  | DIESEL | 11kV | CONNECTED | 0.5
WOOTTON ROAD PROJECT_615 |  | OXFORD |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.24
BLEDINGTON PROJECT_110 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.188
CHARLBURY PROJECT_108 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 4.3
CHARLBURY PROJECT_621 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.078
CHIPPING NORTON PROJECT_613 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.05
DEDDINGTON PROJECT_650 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.05
EYNSHAM PROJECT_92 |  | WITNEY & YARNTON |  | DIESEL | 11kV | CONNECTED | 1
KIDDINGTON PROJECT_624 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.179
STANDLAKE PROJECT_85 |  | WITNEY & YARNTON |  | LANDFILL GAS | 11kV | CONNECTED | 2
WINDRUSH PARK PROJECT_637 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.03
WITNEY & YARNTON PROJECT_105 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 11.85
WITNEY & YARNTON PROJECT_106 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12.5
WITNEY & YARNTON PROJECT_107 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
WITNEY & YARNTON PROJECT_113 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.95
WITNEY & YARNTON PROJECT_127 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 6
WITNEY & YARNTON PROJECT_565 |  | WITNEY & YARNTON |  | PV & BATTERY | 33kV | ACCEPTED | 13.5
WITNEY & YARNTON PROJECT_566 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 21.5
WITNEY & YARNTON PROJECT_592 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 18
WITNEY & YARNTON PROJECT_617 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.05
WITNEY & YARNTON PROJECT_627 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.05
WITNEY & YARNTON PROJECT_629 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.015
WITNEY & YARNTON PROJECT_630 |  | WITNEY & YARNTON |  | CHP - GAS TURBINE | 11kV | CONNECTED | 1
WITNEY & YARNTON PROJECT_88 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 35
WOODSTOCK PROJECT_611 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.51
YARNTON PROJECT_114 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 4.98
BOSTON MANOR PROJECT_133 |  | BOSTON MANOR |  | OTHER SYNCHRONOUS | 11kV | CONNECTED | 7.5
BOSTON MANOR PROJECT_135 |  | BOSTON MANOR |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 1
HARVARD LANE PROJECT_136 |  | EALING (D) |  | GAS TURBINE | 11kV | CONNECTED | 1.6
IRONBRIDGE PROJECT_134 |  | IRONBRIDGE |  | DIESEL | 11kV | CONNECTED | 1.012
BICESTER NORTH PROJECT_568 |  | BICESTER NORTH |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 44
BICESTER NORTH PROJECT_638 |  | BICESTER NORTH |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.499
BICESTER NORTH PROJECT_90 |  | BICESTER NORTH |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 17.16
BICESTER PROJECT_111 |  | BICESTER NORTH |  | CHP - GAS TURBINE | 11kV | CONNECTED | 3.169
BICESTER PROJECT_117 |  | BICESTER NORTH |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.899
BICESTER PROJECT_142 |  | BICESTER NORTH |  | CHP - GAS TURBINE | 11kV | CONNECTED | 3.169
BICESTER PROJECT_625 |  | BICESTER NORTH |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.023
BICESTER PROJECT_648 |  | BICESTER NORTH |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.001
BICESTER PROJECT_651 |  | BICESTER NORTH |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.25
BICESTER PROJECT_97 |  | BICESTER NORTH |  | WASTE TO ENERGY | 33kV | CONNECTED | 26
COTTISFORD PROJECT_139 |  | BICESTER NORTH |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
COTTISFORD PROJECT_87 |  | BICESTER NORTH |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
UPPER HEYFORD PROJECT_116 |  | BICESTER NORTH |  | LANDFILL GAS | 11kV | CONNECTED | 1.57
UPPER HEYFORD PROJECT_119 |  | BICESTER NORTH |  | LANDFILL GAS | 11kV | ACCEPTED | 1
UPPER HEYFORD PROJECT_143 |  | BICESTER NORTH |  | LANDFILL GAS | 11kV | CONNECTED | 1.57
UPPER HEYFORD PROJECT_83 |  | BICESTER NORTH |  | LANDFILL GAS | 11kV | CONNECTED | 3.25
BINSTEAD PROJECT_175 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.85
COWES & WOOTTON COMMON PROJECT_146 |  | COWES & WOOTTON COMMON |  | NATURAL GAS | 33kV | CONNECTED | 33
COWES & WOOTTON COMMON PROJECT_152 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8.8
COWES & WOOTTON COMMON PROJECT_153 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
COWES & WOOTTON COMMON PROJECT_154 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
COWES & WOOTTON COMMON PROJECT_159 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
COWES & WOOTTON COMMON PROJECT_165 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8.1
COWES & WOOTTON COMMON PROJECT_730 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.003
COWES PROJECT_164 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3.5
FRESHWATER PROJECT_171 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.2
FRESHWATER PROJECT_172 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.25
NEWPORT PROJECT_147 |  | COWES & WOOTTON COMMON |  | LANDFILL GAS | 11kV | CONNECTED | 1.2
NEWPORT PROJECT_148 |  | COWES & WOOTTON COMMON |  | NATURAL GAS | 11kV | CONNECTED | 2.5
NEWPORT PROJECT_169 |  | COWES & WOOTTON COMMON |  | NATURAL GAS | 11kV | CONNECTED | 0.65
NEWPORT PROJECT_173 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.25
NEWPORT PROJECT_174 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.25
NEWPORT PROJECT_177 |  | COWES & WOOTTON COMMON |  | NATURAL GAS | 11kV | CONNECTED | 0.5
RYDE PROJECT_151 |  | COWES & WOOTTON COMMON |  | NATURAL GAS | 11kV | CONNECTED | 1.25
SANDOWN PROJECT_176 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.98
SHALFLEET PROJECT_162 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.5
SHALFLEET PROJECT_718 |  | COWES & WOOTTON COMMON |  | WIND FARM | 11kV | ACCEPTED | 0.25
SHANKLIN PROJECT_163 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2.8
WOOTTON COMMON PROJECT_166 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6.89
WOOTTON COMMON PROJECT_167 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
BUTTS ASH PROJECT_149 |  | LANGLEY |  | LANDFILL GAS | 11kV | CONNECTED | 11.5
LANGLEY PROJECT_161 |  | LANGLEY |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
LANGLEY PROJECT_170 |  | LANGLEY |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3
LANGLEY PROJECT_715 |  | LANGLEY |  | OTHER SYNCHRONOUS | 11kV | ACCEPTED | 0.33
ALDERSHOT PROJECT_179 |  | ALDERSHOT |  | LANDFILL GAS | 11kV | CONNECTED | 2.4
MILFORD PROJECT_198 |  | ALDERSHOT |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.177
TONGHAM PROJECT_178 |  | ALDERSHOT |  | LANDFILL GAS | 11kV | CONNECTED | 1.33
TONGHAM PROJECT_215 |  | ALDERSHOT |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.41
ALTON & FERNHURST PROJECT_184 |  | ALTON & FERNHURST |  | NATURAL GAS | 33kV | CONNECTED | 15
ALTON & FERNHURST PROJECT_195 |  | ALTON & FERNHURST |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
ALTON & FERNHURST PROJECT_196 |  | ALTON & FERNHURST |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7.92
ALTON & FERNHURST PROJECT_202 |  | ALTON & FERNHURST |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
ALTON & FERNHURST PROJECT_203 |  | ALTON & FERNHURST |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8.3
ALTON & FERNHURST PROJECT_211 |  | ALTON & FERNHURST |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
ALTON & FERNHURST PROJECT_240 |  | ALTON & FERNHURST |  | NATURAL GAS | 33kV | ACCEPTED | 20
ALTON & FERNHURST PROJECT_602 |  | ALTON & FERNHURST |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 9.975
ALTON LOCAL PROJECT_197 |  | ALTON & FERNHURST |  | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.25
FIVE OAKS PROJECT_180 |  | ALTON & FERNHURST |  | NATURAL GAS | 11kV | CONNECTED | 6.4
FIVE OAKS PROJECT_181 |  | ALTON & FERNHURST |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
HERRIARD PROJECT_182 |  | ALTON & FERNHURST |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
HERRIARD PROJECT_216 |  | ALTON & FERNHURST |  | ANAEROBIC DIGESTER | 11kV | CONNECTED | 2.4
LANGLEY COURT PROJECT_608 |  | ALTON & FERNHURST |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.217
MIDHURST PROJECT_185 |  | ALTON & FERNHURST |  | NATURAL GAS | 11kV | CONNECTED | 5
PETERSFIELD PROJECT_204 |  | ALTON & FERNHURST |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.25
PLAISTOW PROJECT_655 |  | ALTON & FERNHURST |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.322
PRESTON CANDOVER PROJECT_609 |  | ALTON & FERNHURST |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 20
BRACKNELL MAIN PROJECT_212 |  | BRACKNELL MAIN |  | DIESEL | 33kV | CONNECTED | 20
BRACKNELL MAIN PROJECT_217 |  | BRACKNELL MAIN |  | GAS TURBINE | 33kV | CONNECTED | 20
BRACKNELL RESERVE PROJECT_189 |  | BRACKNELL RESERVE |  | NATURAL GAS | 33kV | CONNECTED | 47.5
MVEE PROJECT_186 |  | BRACKNELL RESERVE |  | LANDFILL GAS | 11kV | CONNECTED | 1.33
MVEE PROJECT_194 |  | BRACKNELL RESERVE |  | ANAEROBIC DIGESTER | 11kV | CONNECTED | 2.38
BURGHFIELD MAIN PROJECT_200 |  | BURGHFIELD MAIN |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
COURAGES PROJECT_187 |  | BURGHFIELD MAIN |  | WIND FARM | 11kV | CONNECTED | 2.2
COURAGES PROJECT_193 |  | BURGHFIELD MAIN |  | DIESEL | 11kV | ACCEPTED | 1.5
COURAGES PROJECT_218 |  | BURGHFIELD MAIN |  | DIESEL | 11kV | ACCEPTED | 2
GORING PROJECT_222 |  | BURGHFIELD RESERVE |  | NATURAL GAS | 11kV | ACCEPTED | 0.36
SOUTHCOTE PROJECT_221 |  | BURGHFIELD RESERVE |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.21
THEALE PROJECT_219 |  | BURGHFIELD RESERVE |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.25
THEALE PROJECT_220 |  | BURGHFIELD RESERVE |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.06
TRASH GREEN PROJECT_207 |  | BURGHFIELD RESERVE |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.7
CAMBERLEY PROJECT_235 |  | CAMBERLEY MAIN |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 0
FRIMLEY PROJECT_190 |  | CAMBERLEY RESERVE |  | LANDFILL GAS | 11kV | CONNECTED | 1.4
COXMOOR WOOD PROJECT_205 |  | COXMOOR WOOD |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.3
COXMOOR WOOD PROJECT_213 |  | COXMOOR WOOD |  | NATURAL GAS | 33kV | CONNECTED | 16
COXMOOR WOOD PROJECT_214 |  | COXMOOR WOOD |  | NATURAL GAS | 33kV | CONNECTED | 16
COXMOOR WOOD PROJECT_223 |  | COXMOOR WOOD |  | NATURAL GAS | 33kV | ACCEPTED | 16
COXMOOR WOOD PROJECT_229 |  | COXMOOR WOOD |  | PV & BATTERY | 33kV | CONNECTED | 6.2
HITCHES LANE PROJECT_199 |  | COXMOOR WOOD |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.26
WRECCLESHAM PROJECT_232 |  | COXMOOR WOOD |  | BATTERY | 33kV | ACCEPTED | 20
BRAYWICK ROAD PROJECT_224 |  | MAIDENHEAD |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.075
MAIDENHEAD PROJECT_206 |  | MAIDENHEAD |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 0.143
NORTHUMBERLAND AVENUE PROJECT_191 |  | READING |  | LANDFILL GAS | 11kV | CONNECTED | 3
READING PROJECT_201 |  | READING |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.08
READING PROJECT_226 |  | READING |  | SMALL HYDRO | 11kV | ACCEPTED | 0.1
READING PROJECT_227 |  | READING |  | DIESEL | 11kV | ACCEPTED | 0.44
READING PROJECT_228 |  | READING |  | DIESEL | 11kV | ACCEPTED | 0.6
READING PROJECT_230 |  | READING |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 11
SILVER STREET PROJECT_192 |  | READING |  | DIESEL | 11kV | ACCEPTED | 7
TWYFORD PROJECT_225 |  | READING |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 0.1
READING TOWN PROJECT_208 |  | READING TOWN |  | ANAEROBIC DIGESTER | 11kV | CONNECTED | 0.5
THE MALL PROJECT_209 |  | READING TOWN |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.149
CHALVEY PROJECT_251 |  | CHALVEY |  | LANDFILL GAS | 11kV | CONNECTED | 2.5
CHALVEY PROJECT_576 |  | CHALVEY |  | BATTERY | 33kV | ACCEPTED | 49.5
CHALVEY PROJECT_606 |  | CHALVEY |  | BATTERY | 11kV | ACCEPTED | 6.3
PETERSFIELD AVENUE PROJECT_243 |  | CHALVEY |  | NATURAL GAS | 11kV | CONNECTED | 1.94
PETERSFIELD AVENUE PROJECT_564 |  | CHALVEY |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 2
DENHAM PROJECT_255 |  | DENHAM |  | BATTERY | 22kV | ACCEPTED | 20
DENHAM PROJECT_259 |  | DENHAM |  | GAS TURBINE | 22kV | ACCEPTED | 20
LONGFORD PROJECT_245 |  | LONGFORD |  | WASTE TO ENERGY | 33kV | CONNECTED | 45.7
FARNHAM ROYAL PROJECT_246 |  | SLOUGH |  | WASTE TO ENERGY | 11kV | CONNECTED | 12
SLOUGH PROJECT_247 |  | SLOUGH |  | OTHER SYNCHRONOUS | 33kV | CONNECTED | 60
SLOUGH PROJECT_260 |  | SLOUGH |  | STEAM TURBINE | 33kV | ACCEPTED | 46
SUTTON LANE PROJECT_248 |  | UPTON |  | CHP - GAS TURBINE | 11kV | CONNECTED | 4.5
SUTTON LANE PROJECT_249 |  | UPTON |  | WASTE TO ENERGY | 11kV | CONNECTED | 1.5
SUTTON LANE PROJECT_250 |  | UPTON |  | LANDFILL GAS | 11kV | CONNECTED | 2.8
UPTON PROJECT_253 |  | UPTON |  | GAS TURBINE | 11kV | ACCEPTED | 0.4
ASHFORD COMMON PROJECT_263 |  | EAST BEDFONT A |  | DIESEL | 22kV | CONNECTED | 6
CAUSEWAY PROJECT_262 |  | STAINES |  | LANDFILL GAS | 11kV | CONNECTED | 3.5
CAUSEWAY PROJECT_266 |  | STAINES |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2.6
SIDNEY ROAD PROJECT_264 |  | STAINES |  | NATURAL GAS | 11kV | CONNECTED | 1.3
STAINES PROJECT_269 |  | STAINES |  | BATTERY | 33kV | ACCEPTED | 49
STAINES PROJECT_271 |  | STAINES |  | BATTERY | 33kV | ACCEPTED | 49
STAINES PROJECT_562 |  | STAINES |  | BATTERY | 33kV | ACCEPTED | 49.9
SUNBURY CROSS PROJECT_265 |  | STAINES |  | OTHER SYNCHRONOUS | 11kV | CONNECTED | 10
SUNBURY CROSS PROJECT_267 |  | STAINES |  | WASTE TO ENERGY | 11kV | ACCEPTED | 3.7
SUNBURY CROSS PROJECT_268 |  | STAINES |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 1.7
ASHLING ROAD PROJECT_296 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.1
ASHLING ROAD PROJECT_689 |  | CHICHESTER & HUNSTON |  | CHP - GAS TURBINE | 11kV | CONNECTED | 1.8
BILSHAM PROJECT_291 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 15
BILSHAM PROJECT_293 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3
BILSHAM PROJECT_294 |  | CHICHESTER & HUNSTON |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 0.772
BILSHAM PROJECT_302 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.2
BILSHAM PROJECT_708 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 15
CHICHESTER & HUNSTON PROJECT_283 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
CHICHESTER & HUNSTON PROJECT_285 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6
CHICHESTER & HUNSTON PROJECT_290 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
CHICHESTER & HUNSTON PROJECT_292 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8
CHICHESTER & HUNSTON PROJECT_295 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8
CHICHESTER & HUNSTON PROJECT_298 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
CHICHESTER & HUNSTON PROJECT_301 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7
CHICHESTER & HUNSTON PROJECT_303 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4
CHICHESTER & HUNSTON PROJECT_308 |  | CHICHESTER & HUNSTON |  | PV & BATTERY | 33kV | CONNECTED | 7
CHICHESTER & HUNSTON PROJECT_581 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 15
CHICHESTER & HUNSTON PROJECT_677 |  | CHICHESTER & HUNSTON |  | BATTERY | 33kV | CONNECTED | 7
CHICHESTER PROJECT_272 |  | CHICHESTER & HUNSTON |  | NATURAL GAS | 11kV | CONNECTED | 8.6
CHICHESTER PROJECT_273 |  | CHICHESTER & HUNSTON |  | LANDFILL GAS | 11kV | CONNECTED | 3.75
CHICHESTER PROJECT_305 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
HUNSTON PROJECT_281 |  | CHICHESTER & HUNSTON |  | DIESEL | 11kV | CONNECTED | 2
HUNSTON PROJECT_312 |  | CHICHESTER & HUNSTON |  | BATTERY | 11kV | ACCEPTED | 10
HUNSTON PROJECT_580 |  | CHICHESTER & HUNSTON |  | GAS TURBINE | 11kV | ACCEPTED | 6
HUNSTON PROJECT_688 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.035
HUNSTON PROJECT_694 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4
HUNSTON PROJECT_705 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.8
HUNSTON PROJECT_707 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.5
HUNTERS RACE PV PROJECT_287 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 9.45
MANOR FARM SHRIPNEY PV GENERATION PROJECT_299 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8
ROSE GREEN PROJECT_274 |  | CHICHESTER & HUNSTON |  | DIESEL | 11kV | CONNECTED | 5
ROSE GREEN PROJECT_275 |  | CHICHESTER & HUNSTON |  | LANDFILL GAS | 11kV | CONNECTED | 3.045
SOUTH BERSTED PROJECT_672 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0
SOUTH BERSTED PROJECT_696 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.313
FAREHAM MAIN PROJECT_306 |  | FAREHAM MAIN |  | DIESEL | 33kV | CONNECTED | 20
FAREHAM MAIN PROJECT_313 |  | FAREHAM MAIN |  | BATTERY | 33kV | ACCEPTED | 40
FAREHAM MAIN PROJECT_699 |  | FAREHAM MAIN |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0
FAREHAM PROJECT_286 |  | FAREHAM MAIN |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 17.5
HOEFORD PROJECT_669 |  | FAREHAM MAIN |  | CHP - GAS TURBINE | 0.4kV | ACCEPTED | 0.5
PLESSEY, TITCHFIELD PROJECT_284 |  | FAREHAM MAIN |  | DIESEL | 33kV | CONNECTED | 24
TITCHFIELD PROJECT_698 |  | FAREHAM MAIN |  | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.15
TITCHFIELD PROJECT_712 |  | FAREHAM MAIN |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.171
FAREHAM RESERVE PROJECT_668 |  | FAREHAM RESERVE |  | CHP - GAS TURBINE | 33kV | ACCEPTED | 30.56
BROCKHAMPTON PROJECT_276 |  | HAVANT |  | CHP - GAS TURBINE | 11kV | CONNECTED | 3.3
BROCKHAMPTON PROJECT_282 |  | HAVANT |  | NATURAL GAS | 11kV | CONNECTED | 5
BROCKHAMPTON PROJECT_314 |  | HAVANT |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 5.32
BROCKHAMPTON PROJECT_667 |  | HAVANT |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0
BROCKHAMPTON PROJECT_687 |  | HAVANT |  | CHP - GAS TURBINE | 11kV | CONNECTED | 3
EMSWORTH PROJECT_665 |  | HAVANT |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.8
EMSWORTH PROJECT_690 |  | HAVANT |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.065
GABLE HEAD PROJECT_711 |  | HAVANT |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.24
HAVANT PROJECT_300 |  | HAVANT |  | DIESEL | 33kV | CONNECTED | 20
HAVANT PROJECT_309 |  | HAVANT |  | CHP - GAS TURBINE | 33kV | CONNECTED | 20
HORNDEAN PROJECT_289 |  | HAVANT |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
HORNDEAN PROJECT_709 |  | HAVANT |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
LEIGH PARK PROJECT_277 |  | HAVANT |  | LANDFILL GAS | 11kV | CONNECTED | 3.5
LEIGH PARK PROJECT_697 |  | HAVANT |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.243
FRATTON PARK PROJECT_700 |  | PORTSMOUTH |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0
GREETHAM STREET PROJECT_678 |  | PORTSMOUTH |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.03
GREETHAM STREET PROJECT_679 |  | PORTSMOUTH |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0.05
GREETHAM STREET PROJECT_702 |  | PORTSMOUTH |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.12
HILSEA INCINERATOR PROJECT_278 |  | PORTSMOUTH |  | WASTE TO ENERGY | 33kV | CONNECTED | 20
PORTSMOUTH PROJECT_288 |  | PORTSMOUTH |  | OTHER SYNCHRONOUS | 33kV | CONNECTED | 1
PORTSMOUTH PROJECT_675 |  | PORTSMOUTH |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.25
PORTSMOUTH PROJECT_680 |  | PORTSMOUTH |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0.015
PORTSMOUTH PROJECT_701 |  | PORTSMOUTH |  | CHP - GAS TURBINE | 33kV | CONNECTED | 0
GAMBLE ROAD PROJECT_666 |  | WYMERING & FORT WIDLEY |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.8
HILSEA PROJECT_660 |  | WYMERING & FORT WIDLEY |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.15
HILSEA PROJECT_683 |  | WYMERING & FORT WIDLEY |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.108
HILSEA PROJECT_684 |  | WYMERING & FORT WIDLEY |  | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.069
PORTCHESTER PROJECT_279 |  | WYMERING & FORT WIDLEY |  | LANDFILL GAS | 11kV | CONNECTED | 3.5
SOUTHWICK ESTATE PV PROJECT_297 |  | WYMERING & FORT WIDLEY |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 40
WATERLOOVILLE PROJECT_681 |  | WYMERING & FORT WIDLEY |  | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.05
WYMERING & FORT WIDLEY PROJECT_307 |  | WYMERING & FORT WIDLEY |  | DIESEL | 33kV | CONNECTED | 19.85
WYMERING & FORT WIDLEY PROJECT_310 |  | WYMERING & FORT WIDLEY |  | LANDFILL GAS | 33kV | ACCEPTED | 20
WYMERING PROJECT_280 |  | WYMERING & FORT WIDLEY |  | CHP - GAS TURBINE | 11kV | CONNECTED | 4
WYMERING PROJECT_673 |  | WYMERING & FORT WIDLEY |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0
WYMERING PROJECT_674 |  | WYMERING & FORT WIDLEY |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0.135
LYMINGTON PROJECT_361 |  | ARNEWOOD |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2
LYMINGTON PROJECT_372 |  | ARNEWOOD |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.17
NEW MILTON PROJECT_332 |  | ARNEWOOD |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.7
NEW MILTON PROJECT_378 |  | ARNEWOOD |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.05
ALDERNEY PROJECT_315 |  | BOURNEMOUTH |  | LANDFILL GAS | 11kV | CONNECTED | 7.5
ALDERNEY PROJECT_316 |  | BOURNEMOUTH |  | NATURAL GAS | 11kV | CONNECTED | 1.4
CENTRAL PROJECT_331 |  | BOURNEMOUTH |  | CHP - GAS TURBINE | 11kV | DISCONNECTED | 5.4
ELECTRIC HOUSE PROJECT_374 |  | BOURNEMOUTH |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.25
CHRISTCHURCH PROJECT_330 |  | CHRISTCHURCH |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7.5
CHRISTCHURCH PROJECT_355 |  | CHRISTCHURCH |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
CHRISTCHURCH PROJECT_368 |  | CHRISTCHURCH |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 3
SOMERFORD PROJECT_375 |  | CHRISTCHURCH |  | OTHER SYNCHRONOUS | 11kV | CONNECTED | 1
BLANDFORD PROJECT_397 |  | LYTCHETT |  | GAS | 11kV | ACCEPTED | 0
BLANDFORD PROJECT_398 |  | LYTCHETT |  | DIESEL | 11kV | ACCEPTED | 0
CORFE MULLEN PROJECT_317 |  | LYTCHETT |  | LANDFILL GAS | 11kV | CONNECTED | 1.15
CREEKMOOR PROJECT_359 |  | LYTCHETT |  | WASTE TO ENERGY | 11kV | CONNECTED | 1.024
HOLES BAY PROJECT_373 |  | LYTCHETT |  | BATTERY | 11kV | ACCEPTED | 7.5
HOLES BAY PROJECT_385 |  | LYTCHETT |  | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.37
LYTCHETT PROJECT_338 |  | LYTCHETT |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 3.3
LYTCHETT PROJECT_339 |  | LYTCHETT |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7.2
LYTCHETT PROJECT_340 |  | LYTCHETT |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
LYTCHETT PROJECT_343 |  | LYTCHETT |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12.8
LYTCHETT PROJECT_346 |  | LYTCHETT |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 9.36
LYTCHETT PROJECT_360 |  | LYTCHETT |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
LYTCHETT PROJECT_395 |  | LYTCHETT |  | BATTERY | 33kV | ACCEPTED | 25
LYTCHETT PROJECT_583 |  | LYTCHETT |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 12
MANNINGTON PROJECT_319 |  | MANNINGTON |  | LANDFILL GAS | 33kV | CONNECTED | 3.16
MANNINGTON PROJECT_341 |  | MANNINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.025
MANNINGTON PROJECT_342 |  | MANNINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 11.2
MANNINGTON PROJECT_347 |  | MANNINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 11
MANNINGTON PROJECT_348 |  | MANNINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 16
MANNINGTON PROJECT_356 |  | MANNINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.032
MANNINGTON PROJECT_386 |  | MANNINGTON |  | BATTERY | 33kV | ACCEPTED | 49.9
MANNINGTON PROJECT_393 |  | MANNINGTON |  | PHOTOVOLTAIC PLANT + BATTERY STORAGE | 33kV | ACCEPTED | 8
MILL LANE PROJECT_318 |  | MANNINGTON |  | LANDFILL GAS | 11kV | CONNECTED | 1
MILL LANE PROJECT_571 |  | MANNINGTON |  | LANDFILL GAS | 11kV | ACCEPTED | 7.6
VERWOOD PROJECT_394 |  | MANNINGTON |  | GAS | 11kV | ACCEPTED | 5
POOLE (HILL STREET) PROJECT_379 |  | POOLE PS (HAMWORTHY) |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 0
POOLE (HILL STREET) PROJECT_390 |  | POOLE PS (HAMWORTHY) |  | DIESEL | 11kV | ACCEPTED | 3.4
REDHILL PROJECT_324 |  | REDHILL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 20.31
REDHILL PROJECT_352 |  | REDHILL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 24.8
REDHILL PROJECT_353 |  | REDHILL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5.9
REDHILL PROJECT_354 |  | REDHILL |  | ANAEROBIC DIGESTER | 33kV | ACCEPTED | 5
REDHILL PROJECT_363 |  | REDHILL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 3.5
REDHILL PROJECT_364 |  | REDHILL |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.9
REDHILL PROJECT_365 |  | REDHILL |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3.81
REDHILL PROJECT_387 |  | REDHILL |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 3.7
WINTON PROJECT_320 |  | REDHILL |  | DIESEL | 11kV | CONNECTED | 5.061
REDLYNCH PROJECT_327 |  | SALISBURY |  | LANDFILL GAS | 11kV | CONNECTED | 0.6
REDLYNCH PROJECT_328 |  | SALISBURY |  | LANDFILL GAS | 11kV | CONNECTED | 1
REDLYNCH PROJECT_337 |  | SALISBURY |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 6
SALISBURY PROJECT_325 |  | SALISBURY |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 9.25
SALISBURY PROJECT_572 |  | SALISBURY |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 12.5
BOURTON PROJECT_335 |  | SHAFTESBURY |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.5
SHAFTESBURY PROJECT_323 |  | SHAFTESBURY |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8.6
SHAFTESBURY PROJECT_326 |  | SHAFTESBURY |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12
SHAFTESBURY PROJECT_349 |  | SHAFTESBURY |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.5
SHAFTESBURY PROJECT_357 |  | SHAFTESBURY |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.5
SHAFTESBURY PROJECT_358 |  | SHAFTESBURY |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4
SHAFTESBURY PROJECT_366 |  | SHAFTESBURY |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.5
SHAFTESBURY PROJECT_367 |  | SHAFTESBURY |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 4.125
SHAFTESBURY PROJECT_370 |  | SHAFTESBURY |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.08
SHAFTESBURY PROJECT_377 |  | SHAFTESBURY |  | BATTERY | 33kV | ACCEPTED | 20
SHAFTESBURY PROJECT_384 |  | SHAFTESBURY |  | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.237
SHAFTESBURY PROJECT_392 |  | SHAFTESBURY |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 11
SHROTON PROJECT_334 |  | SHAFTESBURY |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 6.6
WINCANTON PROJECT_336 |  | SHAFTESBURY |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
BOVINGTON PROJECT_396 |  | WAREHAM |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
WAREHAM PROJECT_321 |  | WAREHAM |  | LANDFILL GAS | 33kV | CONNECTED | 3.23
WAREHAM PROJECT_329 |  | WAREHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6
WAREHAM PROJECT_345 |  | WAREHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 9
WAREHAM PROJECT_350 |  | WAREHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 3.96
WAREHAM PROJECT_351 |  | WAREHAM |  | LANDFILL GAS | 33kV | ACCEPTED | 20.8
WAREHAM PROJECT_573 |  | WAREHAM |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 0
WAREHAM TOWN PROJECT_376 |  | WAREHAM |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.1
ANDOVER PROJECT_52 |  | ANDOVER |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
ANDOVER PROJECT_53 |  | ANDOVER |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 14.31
ANDOVER PROJECT_59 |  | ANDOVER |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 39.3
ANDOVER PROJECT_60 |  | ANDOVER |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 3.5
MIDDLE WALLOP PROJECT_55 |  | ANDOVER |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.4
MIDDLE WALLOP PROJECT_61 |  | ANDOVER |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.4
PORTWAY PROJECT_51 |  | ANDOVER |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 6.3
PORTWAY PROJECT_64 |  | ANDOVER |  | DIESEL | 11kV | CONNECTED | 1.76
CALNE PROJECT_405 |  | CHIPPENHAM |  | LANDFILL GAS | 11kV | CONNECTED | 2.5
CALNE PROJECT_406 |  | CHIPPENHAM |  | LANDFILL GAS | 11kV | CONNECTED | 2.5
CALNE PROJECT_461 |  | CHIPPENHAM |  | GAS TURBINE | 11kV | ACCEPTED | 7.5
CHIPPENHAM PROJECT_399 |  | CHIPPENHAM |  | NATURAL GAS | 33kV | CONNECTED | 12
CHIPPENHAM PROJECT_401 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
CHIPPENHAM PROJECT_402 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.5
CHIPPENHAM PROJECT_408 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6.5
CHIPPENHAM PROJECT_409 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12
CHIPPENHAM PROJECT_414 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6.1
CHIPPENHAM PROJECT_421 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 11
CHIPPENHAM PROJECT_422 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7
CHIPPENHAM PROJECT_426 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12
CHIPPENHAM PROJECT_464 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 40
CHIPPENHAM PROJECT_584 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 42
CHIPPENHAM PROJECT_595 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 42.11
LYNEHAM PROJECT_407 |  | CHIPPENHAM |  | DIESEL | 11kV | CONNECTED | 2.75
MALMESBURY PROJECT_455 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.5
SUTTON BENGER PROJECT_589 |  | CHIPPENHAM |  | BATTERY | 11kV | ACCEPTED | 0.914
BRUTON PROJECT_449 |  | FROME |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.202
CODFORD PROJECT_418 |  | FROME |  | ANAEROBIC DIGESTER | 11kV | CONNECTED | 2
CROCKERTON PROJECT_415 |  | FROME |  | STEAM TURBINE | 11kV | CONNECTED | 1
FROME PROJECT_ |  | FROME |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 10.53
FROME PROJECT_413 |  | FROME |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 9.5
FROME PROJECT_420 |  | FROME |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8
FROME PROJECT_423 |  | FROME |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6.5
FROME PROJECT_433 |  | FROME |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
FROME PROJECT_434 |  | FROME |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7
FROME PROJECT_435 |  | FROME |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12.16
FROME PROJECT_442 |  | FROME |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
FROME PROJECT_448 |  | FROME |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0.05
FROME PROJECT_456 |  | FROME |  | BATTERY | 33kV | ACCEPTED | 0.8
FROME PROJECT_457 |  | FROME |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6.35
FROME PROJECT_459 |  | FROME |  | WASTE TO ENERGY | 33kV | ACCEPTED | 26.5
FROME PROJECT_460 |  | FROME |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4
FROME PROJECT_465 |  | FROME |  | BATTERY | 33kV | ACCEPTED | 7
FROME PROJECT_594 |  | FROME |  | GAS TURBINE | 11kV | ACCEPTED | 2.67
HAWKERIDGE PROJECT_450 |  | FROME |  | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.08
HAWKERIDGE PROJECT_451 |  | FROME |  | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.1
HAWKERIDGE PROJECT_578 |  | FROME |  | NATURAL GAS | 11kV | ACCEPTED | 7.56
HAWKERIDGE PROJECT_593 |  | FROME |  | GAS TURBINE | 11kV | ACCEPTED | 7.6
HOLWELL PROJECT_436 |  | FROME |  | WIND FARM | 11kV | CONNECTED | 0.5
HOLWELL PROJECT_437 |  | FROME |  | WIND FARM | 11kV | CONNECTED | 0.5
WESTBURY PROJECT_404 |  | FROME |  | LANDFILL GAS | 11kV | CONNECTED | 4.76
ASHTON PARK PROJECT_443 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
ASHTON PARK PROJECT_713 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.175
AVON RUBBER PROJECT_458 |  | NORRINGTON |  | PV AND BATTERY | 11kV | ACCEPTED | 0.14
BRADFORD-ON-AVON PROJECT_597 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.125
BROMHAM PROJECT_452 |  | NORRINGTON |  | GAS TURBINE | 11kV | CONNECTED | 0.4
CORSHAM PROJECT_416 |  | NORRINGTON |  | OTHER SYNCHRONOUS | 11kV | CONNECTED | 2
DEVIZES PROJECT_429 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.3
DEVIZES PROJECT_598 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.068
MELKSHAM TOWN PROJECT_417 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.5
MELKSHAM TOWN PROJECT_468 |  | NORRINGTON |  | GAS TURBINE | 11kV | ACCEPTED | 7.2
NORRINGTON PROJECT_400 |  | NORRINGTON |  | NATURAL GAS | 33kV | CONNECTED | 5.45
NORRINGTON PROJECT_403 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.5
NORRINGTON PROJECT_419 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
NORRINGTON PROJECT_424 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.5
NORRINGTON PROJECT_425 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 14
NORRINGTON PROJECT_428 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12.16
NORRINGTON PROJECT_430 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
NORRINGTON PROJECT_431 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 13
NORRINGTON PROJECT_432 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
NORRINGTON PROJECT_438 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 20
NORRINGTON PROJECT_440 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.4
NORRINGTON PROJECT_447 |  | NORRINGTON |  | CHP - GAS TURBINE | 33kV | CONNECTED | 0.5
NORRINGTON PROJECT_466 |  | NORRINGTON |  | BATTERY | 33kV | ACCEPTED | 20
NORRINGTON PROJECT_469 |  | NORRINGTON |  | NATURAL GAS | 33kV | CONNECTED | 16
NORRINGTON PROJECT_579 |  | NORRINGTON |  | PV & BATTERY | 33kV | ACCEPTED | 20
SPRING QUARRY WEST PROJECT_445 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 7
SPRING QUARRY WEST PROJECT_467 |  | NORRINGTON |  | GAS TURBINE | 11kV | ACCEPTED | 5
TROWBRIDGE TOWN PROJECT_444 |  | NORRINGTON |  | DIESEL | 11kV | CONNECTED | 2.5
WEST GRAFTON PROJECT_411 |  | WEST GRAFTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5.64
WEST GRAFTON VILLAGE PROJECT_427 |  | WEST GRAFTON |  | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.18
CIRENCESTER PROJECT_480 |  | CIRENCESTER |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
CIRENCESTER PROJECT_481 |  | CIRENCESTER |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7
CIRENCESTER PROJECT_482 |  | CIRENCESTER |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8.7
CIRENCESTER PROJECT_515 |  | CIRENCESTER |  | BATTERY | 33kV | ACCEPTED | 10
CIRENCESTER PROJECT_523 |  | CIRENCESTER |  | PV AND BATTERY | 33kV | ACCEPTED | 10
CIRENCESTER PROJECT_524 |  | CIRENCESTER |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 75
CIRENCESTER PROJECT_588 |  | CIRENCESTER |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 10
CIRENCESTER PROJECT_658 |  | CIRENCESTER |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 24.2
CIRENCESTER TOWN PROJECT_505 |  | CIRENCESTER |  | PV & BATTERY | 11kV | ACCEPTED | 1
GALILEO PROJECT_511 |  | GALILEO |  | BATTERY | 11kV | ACCEPTED | 10
HONDA PROJECT_476 |  | STRATTON MAIN |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 17.9
PARK NORTH PROJECT_519 |  | STRATTON MAIN |  | CHP - SPARK IGNITION | 11kV | ACCEPTED | 1
STRATTON MAIN PROJECT_487 |  | STRATTON MAIN |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 28.6
STRATTON MAIN PROJECT_488 |  | STRATTON MAIN |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 22.6
STRATTON MAIN PROJECT_503 |  | STRATTON MAIN |  | BATTERY | 33kV | ACCEPTED | 20
STANTON FITZWARREN PROJECT_491 |  | STRATTON RESERVE |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
STANTON FITZWARREN PROJECT_492 |  | STRATTON RESERVE |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3.5
STRATTON PROJECT_497 |  | STRATTON RESERVE |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.71
STRATTON PROJECT_498 |  | STRATTON RESERVE |  | DIESEL | 11kV | CONNECTED | 2
STRATTON PROJECT_514 |  | STRATTON RESERVE |  | BATTERY | 11kV | ACCEPTED | 1.36
STRATTON PROJECT_590 |  | STRATTON RESERVE |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.526
STRATTON RESERVE PROJECT_471 |  | STRATTON RESERVE |  | WIND FARM | 33kV | CONNECTED | 6.5
STRATTON RESERVE PROJECT_477 |  | STRATTON RESERVE |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
STRATTON RESERVE PROJECT_478 |  | STRATTON RESERVE |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
STRATTON RESERVE PROJECT_486 |  | STRATTON RESERVE |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 9
SWINDON PROJECT_ |  | SWINDON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 24.53
SWINDON PROJECT_470 |  | SWINDON |  | LANDFILL GAS | 33kV | CONNECTED | 4.64
SWINDON PROJECT_479 |  | SWINDON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
SWINDON PROJECT_484 |  | SWINDON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8
SWINDON PROJECT_485 |  | SWINDON |  | DIESEL | 11kV | CONNECTED | 1.781
SWINDON PROJECT_493 |  | SWINDON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
SWINDON PROJECT_494 |  | SWINDON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
SWINDON PROJECT_502 |  | SWINDON |  | DIESEL | 33kV | CONNECTED | 6
SWINDON PROJECT_507 |  | SWINDON |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 2.5
SWINDON PROJECT_512 |  | SWINDON |  | BATTERY | 11kV | ACCEPTED | 1.2
SWINDON PROJECT_516 |  | SWINDON |  | BATTERY | 33kV | ACCEPTED | 1.5
SWINDON PROJECT_517 |  | SWINDON |  | BATTERY | 33kV | ACCEPTED | 12
SWINDON PROJECT_657 |  | SWINDON |  | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.163
TRADING ESTATE PROJECT_473 |  | SWINDON |  | DIESEL | 11kV | CONNECTED | 0.42
TRADING ESTATE PROJECT_504 |  | SWINDON |  | CHP - SPARK IGNITION | 11kV | CONNECTED | 2.15
WOOTTON BASSETT PROJECT_474 |  | SWINDON |  | WASTE TO ENERGY | 11kV | CONNECTED | 2
WOOTTON BASSETT PROJECT_475 |  | SWINDON |  | LANDFILL GAS | 11kV | CONNECTED | 2
WOOTTON BASSETT PROJECT_483 |  | SWINDON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
WOOTTON BASSETT PROJECT_522 |  | SWINDON |  | LANDFILL GAS | 11kV | ACCEPTED | 6.5
WOOTTON BASSETT PROJECT_659 |  | SWINDON |  | GAS TURBINE | 11kV | ACCEPTED | 7.5
QUARRY ROAD PROJECT_509 |  | TOOTHILL |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 1.8
TOOTHILL PROJECT_472 |  | TOOTHILL |  | LANDFILL GAS | 11kV | CONNECTED | 2
TOOTHILL PROJECT_489 |  | TOOTHILL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 48.51
TOOTHILL PROJECT_490 |  | TOOTHILL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8.2
TOOTHILL PROJECT_495 |  | TOOTHILL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6.76
TOOTHILL PROJECT_508 |  | TOOTHILL |  | BATTERY | 33kV | ACCEPTED | 30
TOOTHILL PROJECT_656 |  | TOOTHILL |  | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.058
WROUGHTON PROJECT_500 |  | TOOTHILL |  | LANDFILL GAS | 11kV | CONNECTED | 2
WROUGHTON PROJECT_501 |  | TOOTHILL |  | LANDFILL GAS | 11kV | CONNECTED | 2
WROUGHTON PROJECT_513 |  | TOOTHILL |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 7
BASSETT PROJECT_719 |  | ROWNHAMS |  | LANDFILL GAS | 11kV | ACCEPTED | 0.21
BASSETT PROJECT_728 |  | ROWNHAMS |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.021
BEVOIS VALLEY PROJECT_532 |  | ROWNHAMS |  | CHP - GAS TURBINE | 6.6kV | CONNECTED | 1
BEVOIS VALLEY PROJECT_722 |  | ROWNHAMS |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0.175
DUNBRIDGE PROJECT_591 |  | ROWNHAMS |  | PV & BATTERY | 0.4kV | ACCEPTED | 0.044
ROWNHAMS PROJECT_535 |  | ROWNHAMS |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
ROWNHAMS PROJECT_537 |  | ROWNHAMS |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.32
ROWNHAMS PROJECT_538 |  | ROWNHAMS |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.99
ROWNHAMS PROJECT_540 |  | ROWNHAMS |  | BATTERY | 33kV | ACCEPTED | 10
ROWNHAMS PROJECT_544 |  | ROWNHAMS |  | BATTERY | 33kV | ACCEPTED | 10
ROWNHAMS PROJECT_545 |  | ROWNHAMS |  | OTHER SYNCHRONOUS | 33kV | ACCEPTED | 20
ROWNHAMS PROJECT_550 |  | ROWNHAMS |  | NATURAL GAS | 33kV | ACCEPTED | 20
ROWNHAMS PROJECT_551 |  | ROWNHAMS |  | NATURAL GAS | 33kV | CONNECTED | 20
EASTLEIGH NORTH PROJECT_528 |  | SOUTHAMPTON MAIN |  | LANDFILL GAS | 11kV | CONNECTED | 2.92
EASTLEIGH NORTH PROJECT_542 |  | SOUTHAMPTON MAIN |  | OTHER SYNCHRONOUS | 0.4kV | CONNECTED | 1
HARESTOCK PROJECT_716 |  | SOUTHAMPTON MAIN |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.42
HARESTOCK PROJECT_726 |  | SOUTHAMPTON MAIN |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.05
SOUTHAMPTON RESERVE PROJECT_525 |  | SOUTHAMPTON RESERVE |  | GEOTHERMAL | 33kV | CONNECTED | 7
SOUTHAMPTON RESERVE PROJECT_546 |  | SOUTHAMPTON RESERVE |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 0.81
SOUTHAMPTON RESERVE PROJECT_714 |  | SOUTHAMPTON RESERVE |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 1.9
SOUTHAMPTON RESERVE PROJECT_723 |  | SOUTHAMPTON RESERVE |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0
SOUTHAMPTON RESERVE PROJECT_727 |  | SOUTHAMPTON RESERVE |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.037
SOUTHAMPTON RESERVE PROJECT_729 |  | SOUTHAMPTON RESERVE |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 0.015
MAYBUSH PROJECT_526 |  | VELMORE |  | NATURAL GAS | 11kV | CONNECTED | 2
REGENTS PARK PROJECT_530 |  | VELMORE |  | WASTE TO ENERGY | 11kV | CONNECTED | 1.2
SILKSTEAD PROJECT_548 |  | VELMORE |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.5
SILKSTEAD PROJECT_717 |  | VELMORE |  | OTHER SYNCHRONOUS | 11kV | ACCEPTED | 0.37
SILKSTEAD PROJECT_720 |  | VELMORE |  | OTHER SYNCHRONOUS | 11kV | ACCEPTED | 0.2
VELMORE PROJECT_531 |  | VELMORE |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6.3
VELMORE PROJECT_539 |  | VELMORE |  | DIESEL | 33kV | ACCEPTED | 20
ST CROSS PROJECT_724 |  | WINCHESTER |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.064
TOTTON PROJECT_549 |  | WINCHESTER |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2
VELMORE PROJECT_529 |  | WINCHESTER |  | DIESEL | 11kV | CONNECTED | 1.5
WESTERN ESPLANADE PROJECT_682 |  | WINCHESTER |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.18
WESTERN ESPLANADE PROJECT_721 |  | WINCHESTER |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.18
WINCHESTER PROJECT_541 |  | WINCHESTER |  | OTHER SYNCHRONOUS | 33kV | ACCEPTED | 20
WINCHESTER PROJECT_577 |  | WINCHESTER |  | BATTERY | 33kV | ACCEPTED | 10
GREENFORD PROJECT_556 |  | GREENFORD |  | NATURAL GAS | 11kV | CONNECTED | 1
FLACKWELL HEATH PROJECT_1 |  |  | FLACKWELL HEATH | LANDFILL GAS | 11kV | CONNECTED | 1.4
WELL END PROJECT_3 |  |  | WELL END | BATTERY | 11kV | ACCEPTED | 7.2
CASTLE CARY PROJECT_12 |  |  | CASTLE CARY | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.32
CASTLE CARY PROJECT_4 |  |  | CASTLE CARY | LANDFILL GAS | 11kV | CONNECTED | 3.8
CHILTON CANTELLO PROJECT_5 |  |  | CHILTON CANTELO | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
HENSTRIDGE PROJECT_11 |  |  | HENSTRIDGE | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.13
HENSTRIDGE PROJECT_13 |  |  | HENSTRIDGE | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.1
MILBORNE PORT PROJECT_20 |  |  | MILBORNE PORT | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
SPARKFORD PROJECT_14 |  |  | SPARKFORD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.2
YEOVIL PROJECT_24 |  |  | YEOVIL | CHP - GAS TURBINE | 11kV | ACCEPTED | 10
YETMINSTER PROJECT_15 |  |  | YETMINSTER | DIESEL | 11kV | CONNECTED | 0.4
YETMINSTER PROJECT_16 |  |  | YETMINSTER | CHP - GAS TURBINE | 11kV | CONNECTED | 0.25
YETMINSTER PROJECT_17 |  |  | YETMINSTER | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.15
BISHOPS WALTHAM PROJECT_27 |  |  | BISHOPS WALTHAM | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
BISHOPS WALTHAM PROJECT_686 |  |  | BISHOPS WALTHAM | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 2.5
HAMBLE PROJECT_33 |  |  | HAMBLE | BATTERY | 11kV | ACCEPTED | 5
HAMBLE PROJECT_585 |  |  | HAMBLE | LANDFILL GAS | 11kV | ACCEPTED | 7.2
WESTON PROJECT_26 |  |  | WESTON | LANDFILL GAS | 11kV | CONNECTED | 2.6
BOSCOMBE DOWN PROJECT_441 |  |  | BOSCOMBE DOWN | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 10
BOSCOMBE DOWN PROJECT_454 |  |  | BOSCOMBE DOWN | DIESEL | 11kV | CONNECTED | 4
BEENHAM PROJECT_54 |  |  | BEENHAM | LANDFILL GAS | 11kV | CONNECTED | 1.9
KINTBURY PROJECT_56 |  |  | KINTBURY | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.2
TADLEY PROJECT_62 |  |  | TADLEY | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.3
THATCHAM PROJECT_49 |  |  | THATCHAM | NATURAL GAS | 11kV | CONNECTED | 9.6
THATCHAM PROJECT_50 |  |  | THATCHAM | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.7
BASINGSTOKE PROJECT_36 |  |  | BASINGSTOKE | WASTE TO ENERGY | 11kV | CONNECTED | 12
BASINGSTOKE PROJECT_37 |  |  | BASINGSTOKE | OTHER SYNCHRONOUS | 11kV | CONNECTED | 0.75
JAYS CLOSE PROJECT_46 |  |  | JAYS CLOSE | DIESEL | 11kV | CONNECTED | 4
ARBORFIELD PROJECT_34 |  |  | ARBORFIELD | LANDFILL GAS | 11kV | CONNECTED | 1
ARBORFIELD PROJECT_35 |  |  | ARBORFIELD | OTHER SYNCHRONOUS | 11kV | CONNECTED | 1.44
CHINEHAM PROJECT_45 |  |  | CHINEHAM | CHP - GAS TURBINE | 11kV | CONNECTED | 1.368
OVERTON PROJECT_39 |  |  | OVERTON | NATURAL GAS | 11kV | CONNECTED | 7.2
OVERTON PROJECT_43 |  |  | OVERTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3.2
OVERTON PROJECT_605 |  |  | OVERTON | CHP - GAS TURBINE | 11kV | ACCEPTED | 1.2
HOUNDMILLS PROJECT_38 |  |  | HOUNDMILLS | NATURAL GAS | 11kV | CONNECTED | 1.3
HOUNDMILLS PROJECT_40 |  |  | HOUNDMILLS | DIESEL | 11kV | CONNECTED | 1.2
CHICKERELL PROJECT_661 |  |  | CHICKERELL | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.069
CHICKERELL PROJECT_692 |  |  | CHICKERELL | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.7
DORCHESTER PROJECT_671 |  |  | DORCHESTER | CHP - GAS TURBINE | 11kV | ACCEPTED | 0
DORCHESTER PROJECT_68 |  |  | DORCHESTER | NATURAL GAS | 11kV | CONNECTED | 1.44
DORCHESTER PROJECT_710 |  |  | DORCHESTER | ANAEROBIC DIGESTER | 11kV | CONNECTED | 0.36
DORCHESTER PROJECT_74 |  |  | DORCHESTER | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.095
DORCHESTER PROJECT_75 |  |  | DORCHESTER | CHP - GAS TURBINE | 0.4kV | ACCEPTED | 0.1
PORTLAND PROJECT_69 |  |  | PORTLAND | DIESEL | 11kV | CONNECTED | 2.4
WEYMOUTH PROJECT_70 |  |  | WEYMOUTH | NATURAL GAS | 11kV | CONNECTED | 3.02
COWLEY LOCAL PROJECT_118 |  |  | COWLEY LOCAL | DIESEL | 11kV | CONNECTED | 0.56
COWLEY LOCAL PROJECT_620 |  |  | COWLEY LOCAL | OTHER SYNCHRONOUS | 11kV | CONNECTED | 0.149
ROSE HILL PROJECT_641 |  |  | ROSE HILL | CHP - GAS TURBINE | 11kV | CONNECTED | 0.8
BERINSFIELD PROJECT_100 |  |  | BERINSFIELD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2
BERINSFIELD PROJECT_109 |  |  | BERINSFIELD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.14
KENNINGTON PROJECT_622 |  |  | KENNINGTON | SMALL HYDRO | 11kV | CONNECTED | 0.4
WALLINGFORD PROJECT_121 |  |  | WALLINGFORD | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.05
WALLINGFORD PROJECT_610 |  |  | WALLINGFORD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.684
WALLINGFORD PROJECT_614 |  |  | WALLINGFORD | LANDFILL GAS | 11kV | CONNECTED | 2.4
WALLINGFORD PROJECT_99 |  |  | WALLINGFORD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.36
CHOLSEY PROJECT_619 |  |  | CHOLSEY | LANDFILL GAS | 11kV | CONNECTED | 0.05
CHOLSEY PROJECT_623 |  |  | CHOLSEY | LANDFILL GAS | 11kV | CONNECTED | 0.25
FULSCOT PROJECT_131 |  |  | FULSCOT | LANDFILL GAS | 11kV | ACCEPTED | 7.56
MILTON PROJECT_612 |  |  | MILTON | LANDFILL GAS | 11kV | CONNECTED | 0.45
MILTON PROJECT_626 |  |  | MILTON | SMALL HYDRO | 11kV | CONNECTED | 0.406
MILTON PROJECT_645 |  |  | MILTON | DIESEL | 11kV | CONNECTED | 1
MILTON PROJECT_649 |  |  | MILTON | DIESEL | 11kV | ACCEPTED | 0.001
MILTON PROJECT_81 |  |  | MILTON | DIESEL | 11kV | CONNECTED | 3.3
MILTON PROJECT_91 |  |  | MILTON | OTHER SYNCHRONOUS | 11kV | CONNECTED | 1.68
WANTAGE PROJECT_616 |  |  | WANTAGE | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.05
WINSMORE LANE PROJECT_647 |  |  | WINSMORE LANE | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.001
ARNCOTT PROJECT_102 |  |  | ARNCOTT | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7.2
ARNCOTT PROJECT_124 |  |  | ARNCOTT | GAS TURBINE | 11kV | ACCEPTED | 5
HEADINGTON PROJECT_93 |  |  | HEADINGTON | CHP - GAS TURBINE | 11kV | CONNECTED | 3.6
OLD ROAD PROJECT_635 |  |  | OLD ROAD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.344
WHEATLEY PROJECT_570 |  |  | WHEATLEY | NATURAL GAS | 11kV | ACCEPTED | 7.12
HIGH WYCOMBE PROJECT_628 |  |  | HIGH WYCOMBE | CHP - GAS TURBINE | 11kV | CONNECTED | 0.07
HIGH WYCOMBE PROJECT_84 |  |  | HIGH WYCOMBE | LANDFILL GAS | 11kV | CONNECTED | 1
WATLINGTON PROJECT_104 |  |  | WATLINGTON | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 17
NORTH HINKSEY PROJECT_618 |  |  | NORTH HINKSEY | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.3
OSNEY PROJECT_636 |  |  | OSNEY | DIESEL | 11kV | CONNECTED | 0.504
ST EBBES PROJECT_631 |  |  | ST EBBES | DIESEL | 11kV | CONNECTED | 0.2
ST EBBES PROJECT_632 |  |  | ST EBBES | DIESEL | 11kV | CONNECTED | 0.5
WOOTTON ROAD PROJECT_615 |  |  | WOOTTON ROAD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.24
BLEDINGTON PROJECT_110 |  |  | BLEDINGTON | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.188
CHARLBURY PROJECT_108 |  |  | CHARLBURY | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 4.3
CHARLBURY PROJECT_621 |  |  | CHARLBURY | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.078
CHIPPING NORTON PROJECT_613 |  |  | CHIPPING NORTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.05
DEDDINGTON PROJECT_650 |  |  | DEDDINGTON | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.05
EYNSHAM PROJECT_92 |  |  | EYNSHAM | DIESEL | 11kV | CONNECTED | 1
KIDDINGTON PROJECT_624 |  |  | KIDDINGTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.179
STANDLAKE PROJECT_85 |  |  | STANDLAKE | LANDFILL GAS | 11kV | CONNECTED | 2
WINDRUSH PARK PROJECT_637 |  |  | WINDRUSH PARK | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.03
WOODSTOCK PROJECT_611 |  |  | WOODSTOCK | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.51
YARNTON PROJECT_114 |  |  | YARNTON | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 4.98
HARVARD LANE PROJECT_136 |  |  | HARVARD LANE | GAS TURBINE | 11kV | CONNECTED | 1.6
BICESTER PROJECT_111 |  |  | BICESTER | CHP - GAS TURBINE | 11kV | CONNECTED | 3.169
BICESTER PROJECT_117 |  |  | BICESTER | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.899
BICESTER PROJECT_142 |  |  | BICESTER | CHP - GAS TURBINE | 11kV | CONNECTED | 3.169
BICESTER PROJECT_625 |  |  | BICESTER | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.023
BICESTER PROJECT_648 |  |  | BICESTER | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.001
BICESTER PROJECT_651 |  |  | BICESTER | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.25
BICESTER PROJECT_97 |  |  | BICESTER | WASTE TO ENERGY | 33kV | CONNECTED | 26
COTTISFORD PROJECT_139 |  |  | COTTISFORD | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
COTTISFORD PROJECT_87 |  |  | COTTISFORD | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
UPPER HEYFORD PROJECT_116 |  |  | UPPER HEYFORD | LANDFILL GAS | 11kV | CONNECTED | 1.57
UPPER HEYFORD PROJECT_119 |  |  | UPPER HEYFORD | LANDFILL GAS | 11kV | ACCEPTED | 1
UPPER HEYFORD PROJECT_143 |  |  | UPPER HEYFORD | LANDFILL GAS | 11kV | CONNECTED | 1.57
UPPER HEYFORD PROJECT_83 |  |  | UPPER HEYFORD | LANDFILL GAS | 11kV | CONNECTED | 3.25
BINSTEAD PROJECT_175 |  |  | BINSTEAD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.85
COWES PROJECT_164 |  |  | COWES POWER STATION | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3.5
FRESHWATER PROJECT_171 |  |  | FRESHWATER | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.2
FRESHWATER PROJECT_172 |  |  | FRESHWATER | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.25
NEWPORT PROJECT_147 |  |  | NEWPORT | LANDFILL GAS | 11kV | CONNECTED | 1.2
NEWPORT PROJECT_148 |  |  | NEWPORT | NATURAL GAS | 11kV | CONNECTED | 2.5
NEWPORT PROJECT_169 |  |  | NEWPORT | NATURAL GAS | 11kV | CONNECTED | 0.65
NEWPORT PROJECT_173 |  |  | NEWPORT | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.25
NEWPORT PROJECT_174 |  |  | NEWPORT | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.25
NEWPORT PROJECT_177 |  |  | NEWPORT | NATURAL GAS | 11kV | CONNECTED | 0.5
RYDE PROJECT_151 |  |  | RYDE | NATURAL GAS | 11kV | CONNECTED | 1.25
SANDOWN PROJECT_176 |  |  | SANDOWN | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.98
SHALFLEET PROJECT_162 |  |  | SHALFLEET | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.5
SHALFLEET PROJECT_718 |  |  | SHALFLEET | WIND FARM | 11kV | ACCEPTED | 0.25
SHANKLIN PROJECT_163 |  |  | SHANKLIN | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2.8
BUTTS ASH PROJECT_149 |  |  | BUTTS ASH | LANDFILL GAS | 11kV | CONNECTED | 11.5
LANGLEY PROJECT_161 |  |  | LANGLEY | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
LANGLEY PROJECT_170 |  |  | LANGLEY | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3
LANGLEY PROJECT_715 |  |  | LANGLEY | OTHER SYNCHRONOUS | 11kV | ACCEPTED | 0.33
ALDERSHOT PROJECT_179 |  |  | ALDERSHOT | LANDFILL GAS | 11kV | CONNECTED | 2.4
MILFORD PROJECT_198 |  |  | MILFORD | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.177
TONGHAM PROJECT_178 |  |  | TONGHAM | LANDFILL GAS | 11kV | CONNECTED | 1.33
TONGHAM PROJECT_215 |  |  | TONGHAM | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.41
ALTON LOCAL PROJECT_197 |  |  | ALTON LOCAL | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.25
FIVE OAKS PROJECT_180 |  |  | FIVE OAKS | NATURAL GAS | 11kV | CONNECTED | 6.4
FIVE OAKS PROJECT_181 |  |  | FIVE OAKS | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
HERRIARD PROJECT_182 |  |  | HERRIARD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
HERRIARD PROJECT_216 |  |  | HERRIARD | ANAEROBIC DIGESTER | 11kV | CONNECTED | 2.4
LANGLEY COURT PROJECT_608 |  |  | LANGLEY COURT | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.217
MIDHURST PROJECT_185 |  |  | MIDHURST | NATURAL GAS | 11kV | CONNECTED | 5
PETERSFIELD PROJECT_204 |  |  | PETERSFIELD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.25
PLAISTOW PROJECT_655 |  |  | PLAISTOW | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.322
PRESTON CANDOVER PROJECT_609 |  |  | PRESTON CANDOVER | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 20
MVEE PROJECT_186 |  |  | MVEE | LANDFILL GAS | 11kV | CONNECTED | 1.33
MVEE PROJECT_194 |  |  | MVEE | ANAEROBIC DIGESTER | 11kV | CONNECTED | 2.38
COURAGES PROJECT_187 |  |  | COURAGES | WIND FARM | 11kV | CONNECTED | 2.2
COURAGES PROJECT_193 |  |  | COURAGES | DIESEL | 11kV | ACCEPTED | 1.5
COURAGES PROJECT_218 |  |  | COURAGES | DIESEL | 11kV | ACCEPTED | 2
GORING PROJECT_222 |  |  | GORING | NATURAL GAS | 11kV | ACCEPTED | 0.36
SOUTHCOTE PROJECT_221 |  |  | SOUTHCOTE | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.21
THEALE PROJECT_219 |  |  | THEALE | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.25
THEALE PROJECT_220 |  |  | THEALE | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.06
TRASH GREEN PROJECT_207 |  |  | TRASH GREEN | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.7
CAMBERLEY PROJECT_235 |  |  | CAMBERLEY | CHP - GAS TURBINE | 11kV | ACCEPTED | 0
FRIMLEY PROJECT_190 |  |  | FRIMLEY | LANDFILL GAS | 11kV | CONNECTED | 1.4
HITCHES LANE PROJECT_199 |  |  | HITCHES LANE | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.26
WRECCLESHAM PROJECT_232 |  |  | WRECCLESHAM | BATTERY | 33kV | ACCEPTED | 20
BRAYWICK ROAD PROJECT_224 |  |  | BRAYWICK ROAD | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.075
NORTHUMBERLAND AVENUE PROJECT_191 |  |  | NORTHUMBERLAND AVENUE | LANDFILL GAS | 11kV | CONNECTED | 3
READING PROJECT_226 |  |  | READING | SMALL HYDRO | 11kV | ACCEPTED | 0.1
READING PROJECT_227 |  |  | READING | DIESEL | 11kV | ACCEPTED | 0.44
READING PROJECT_228 |  |  | READING | DIESEL | 11kV | ACCEPTED | 0.6
SILVER STREET PROJECT_192 |  |  | SILVER STREET | DIESEL | 11kV | ACCEPTED | 7
TWYFORD PROJECT_225 |  |  | TWYFORD | CHP - GAS TURBINE | 11kV | ACCEPTED | 0.1
READING TOWN PROJECT_208 |  |  | READING TOWN | ANAEROBIC DIGESTER | 11kV | CONNECTED | 0.5
THE MALL PROJECT_209 |  |  | THE MALL | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.149
CHALVEY PROJECT_251 |  |  | CHALVEY | LANDFILL GAS | 11kV | CONNECTED | 2.5
CHALVEY PROJECT_606 |  |  | CHALVEY | BATTERY | 11kV | ACCEPTED | 6.3
PETERSFIELD AVENUE PROJECT_243 |  |  | PETERSFIELD AVENUE | NATURAL GAS | 11kV | CONNECTED | 1.94
PETERSFIELD AVENUE PROJECT_564 |  |  | PETERSFIELD AVENUE | CHP - GAS TURBINE | 11kV | ACCEPTED | 2
FARNHAM ROYAL PROJECT_246 |  |  | FARNHAM ROYAL | WASTE TO ENERGY | 11kV | CONNECTED | 12
SUTTON LANE PROJECT_248 |  |  | SUTTON LANE | CHP - GAS TURBINE | 11kV | CONNECTED | 4.5
SUTTON LANE PROJECT_249 |  |  | SUTTON LANE | WASTE TO ENERGY | 11kV | CONNECTED | 1.5
SUTTON LANE PROJECT_250 |  |  | SUTTON LANE | LANDFILL GAS | 11kV | CONNECTED | 2.8
UPTON PROJECT_253 |  |  | UPTON | GAS TURBINE | 11kV | ACCEPTED | 0.4
CAUSEWAY PROJECT_262 |  |  | CAUSEWAY | LANDFILL GAS | 11kV | CONNECTED | 3.5
CAUSEWAY PROJECT_266 |  |  | CAUSEWAY | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2.6
SIDNEY ROAD PROJECT_264 |  |  | SIDNEY ROAD | NATURAL GAS | 11kV | CONNECTED | 1.3
SUNBURY CROSS PROJECT_265 |  |  | SUNBURY CROSS | OTHER SYNCHRONOUS | 11kV | CONNECTED | 10
SUNBURY CROSS PROJECT_267 |  |  | SUNBURY CROSS | WASTE TO ENERGY | 11kV | ACCEPTED | 3.7
SUNBURY CROSS PROJECT_268 |  |  | SUNBURY CROSS | CHP - GAS TURBINE | 11kV | ACCEPTED | 1.7
ASHLING ROAD PROJECT_296 |  |  | ASHLING ROAD | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.1
ASHLING ROAD PROJECT_689 |  |  | ASHLING ROAD | CHP - GAS TURBINE | 11kV | CONNECTED | 1.8
BILSHAM PROJECT_291 |  |  | BILSHAM | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 15
BILSHAM PROJECT_293 |  |  | BILSHAM | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3
BILSHAM PROJECT_294 |  |  | BILSHAM | CHP - GAS TURBINE | 11kV | ACCEPTED | 0.772
BILSHAM PROJECT_302 |  |  | BILSHAM | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.2
BILSHAM PROJECT_708 |  |  | BILSHAM | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 15
CHICHESTER PROJECT_272 |  |  | CHICHESTER | NATURAL GAS | 11kV | CONNECTED | 8.6
CHICHESTER PROJECT_273 |  |  | CHICHESTER | LANDFILL GAS | 11kV | CONNECTED | 3.75
CHICHESTER PROJECT_305 |  |  | CHICHESTER | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
HUNSTON PROJECT_281 |  |  | HUNSTON | DIESEL | 11kV | CONNECTED | 2
HUNSTON PROJECT_312 |  |  | HUNSTON | BATTERY | 11kV | ACCEPTED | 10
HUNSTON PROJECT_580 |  |  | HUNSTON | GAS TURBINE | 11kV | ACCEPTED | 6
ROSE GREEN PROJECT_274 |  |  | ROSE GREEN | DIESEL | 11kV | CONNECTED | 5
ROSE GREEN PROJECT_275 |  |  | ROSE GREEN | LANDFILL GAS | 11kV | CONNECTED | 3.045
SOUTH BERSTED PROJECT_672 |  |  | SOUTH BERSTED | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0
SOUTH BERSTED PROJECT_696 |  |  | SOUTH BERSTED | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.313
HOEFORD PROJECT_669 |  |  | HOEFORD | CHP - GAS TURBINE | 0.4kV | ACCEPTED | 0.5
TITCHFIELD PROJECT_698 |  |  | TITCHFIELD | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.15
TITCHFIELD PROJECT_712 |  |  | TITCHFIELD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.171
BROCKHAMPTON PROJECT_276 |  |  | BROCKHAMPTON | CHP - GAS TURBINE | 11kV | CONNECTED | 3.3
BROCKHAMPTON PROJECT_282 |  |  | BROCKHAMPTON | NATURAL GAS | 11kV | CONNECTED | 5
BROCKHAMPTON PROJECT_314 |  |  | BROCKHAMPTON | CHP - GAS TURBINE | 11kV | ACCEPTED | 5.32
BROCKHAMPTON PROJECT_667 |  |  | BROCKHAMPTON | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0
BROCKHAMPTON PROJECT_687 |  |  | BROCKHAMPTON | CHP - GAS TURBINE | 11kV | CONNECTED | 3
EMSWORTH PROJECT_665 |  |  | EMSWORTH | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.8
EMSWORTH PROJECT_690 |  |  | EMSWORTH | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.065
GABLE HEAD PROJECT_711 |  |  | GABLE HEAD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.24
HORNDEAN PROJECT_289 |  |  | HORNDEAN | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
HORNDEAN PROJECT_709 |  |  | HORNDEAN | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
LEIGH PARK PROJECT_277 |  |  | LEIGH PARK | LANDFILL GAS | 11kV | CONNECTED | 3.5
LEIGH PARK PROJECT_697 |  |  | LEIGH PARK | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.243
FRATTON PARK PROJECT_700 |  |  | FRATTON PARK | CHP - GAS TURBINE | 11kV | CONNECTED | 0
GREETHAM STREET PROJECT_678 |  |  | GREETHAM STREET | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.03
GREETHAM STREET PROJECT_679 |  |  | GREETHAM STREET | CHP - GAS TURBINE | 11kV | CONNECTED | 0.05
GREETHAM STREET PROJECT_702 |  |  | GREETHAM STREET | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.12
PORTSMOUTH PROJECT_288 |  |  | PORTSMOUTH | OTHER SYNCHRONOUS | 33kV | CONNECTED | 1
PORTSMOUTH PROJECT_675 |  |  | PORTSMOUTH | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.25
PORTSMOUTH PROJECT_701 |  |  | PORTSMOUTH | CHP - GAS TURBINE | 33kV | CONNECTED | 0
GAMBLE ROAD PROJECT_666 |  |  | GAMBLE ROAD | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.8
HILSEA PROJECT_660 |  |  | HILSEA | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.15
HILSEA PROJECT_683 |  |  | HILSEA | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.108
HILSEA PROJECT_684 |  |  | HILSEA | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.069
PORTCHESTER PROJECT_279 |  |  | PORTCHESTER | LANDFILL GAS | 11kV | CONNECTED | 3.5
WATERLOOVILLE PROJECT_681 |  |  | WATERLOOVILLE | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.05
WYMERING PROJECT_280 |  |  | WYMERING | CHP - GAS TURBINE | 11kV | CONNECTED | 4
WYMERING PROJECT_673 |  |  | WYMERING | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0
WYMERING PROJECT_674 |  |  | WYMERING | CHP - GAS TURBINE | 11kV | CONNECTED | 0.135
LYMINGTON PROJECT_361 |  |  | LYMINGTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2
LYMINGTON PROJECT_372 |  |  | LYMINGTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.17
NEW MILTON PROJECT_332 |  |  | NEW MILTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.7
NEW MILTON PROJECT_378 |  |  | NEW MILTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.05
ALDERNEY PROJECT_315 |  |  | ALDERNEY | LANDFILL GAS | 11kV | CONNECTED | 7.5
ALDERNEY PROJECT_316 |  |  | ALDERNEY | NATURAL GAS | 11kV | CONNECTED | 1.4
CENTRAL PROJECT_331 |  |  | CENTRAL | CHP - GAS TURBINE | 11kV | DISCONNECTED | 5.4
ELECTRIC HOUSE PROJECT_374 |  |  | ELECTRIC HOUSE | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.25
SOMERFORD PROJECT_375 |  |  | SOMERFORD | OTHER SYNCHRONOUS | 11kV | CONNECTED | 1
BLANDFORD PROJECT_397 |  |  | BLANDFORD | GAS | 11kV | ACCEPTED | 0
BLANDFORD PROJECT_398 |  |  | BLANDFORD | DIESEL | 11kV | ACCEPTED | 0
CORFE MULLEN PROJECT_317 |  |  | CORFE MULLEN | LANDFILL GAS | 11kV | CONNECTED | 1.15
CREEKMOOR PROJECT_359 |  |  | CREEKMOOR | WASTE TO ENERGY | 11kV | CONNECTED | 1.024
HOLES BAY PROJECT_373 |  |  | HOLES BAY | BATTERY | 11kV | ACCEPTED | 7.5
HOLES BAY PROJECT_385 |  |  | HOLES BAY | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.37
MILL LANE PROJECT_318 |  |  | MILL LANE | LANDFILL GAS | 11kV | CONNECTED | 1
MILL LANE PROJECT_571 |  |  | MILL LANE | LANDFILL GAS | 11kV | ACCEPTED | 7.6
VERWOOD PROJECT_394 |  |  | VERWOOD | GAS | 11kV | ACCEPTED | 5
POOLE (HILL STREET) PROJECT_379 |  |  | POOLE (HILL STREET) | CHP - GAS TURBINE | 11kV | ACCEPTED | 0
POOLE (HILL STREET) PROJECT_390 |  |  | POOLE (HILL STREET) | DIESEL | 11kV | ACCEPTED | 3.4
REDHILL PROJECT_364 |  |  | REDHILL | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.9
REDHILL PROJECT_365 |  |  | REDHILL | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3.81
WINTON PROJECT_320 |  |  | WINTON | DIESEL | 11kV | CONNECTED | 5.061
REDLYNCH PROJECT_327 |  |  | REDLYNCH | LANDFILL GAS | 11kV | CONNECTED | 0.6
REDLYNCH PROJECT_328 |  |  | REDLYNCH | LANDFILL GAS | 11kV | CONNECTED | 1
REDLYNCH PROJECT_337 |  |  | REDLYNCH | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 6
BOURTON PROJECT_335 |  |  | BOURTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.5
SHAFTESBURY PROJECT_370 |  |  | SHAFTESBURY | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.08
SHAFTESBURY PROJECT_384 |  |  | SHAFTESBURY | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.237
SHROTON PROJECT_334 |  |  | SHROTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 6.6
WINCANTON PROJECT_336 |  |  | WINCANTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
BOVINGTON PROJECT_396 |  |  | BOVINGTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
WAREHAM TOWN PROJECT_376 |  |  | WAREHAM TOWN | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.1
MIDDLE WALLOP PROJECT_55 |  |  | MIDDLE WALLOP | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.4
MIDDLE WALLOP PROJECT_61 |  |  | MIDDLE WALLOP | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.4
PORTWAY PROJECT_51 |  |  | PORTWAY | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 6.3
PORTWAY PROJECT_64 |  |  | PORTWAY | DIESEL | 11kV | CONNECTED | 1.76
CALNE PROJECT_405 |  |  | CALNE | LANDFILL GAS | 11kV | CONNECTED | 2.5
CALNE PROJECT_406 |  |  | CALNE | LANDFILL GAS | 11kV | CONNECTED | 2.5
CALNE PROJECT_461 |  |  | CALNE | GAS TURBINE | 11kV | ACCEPTED | 7.5
LYNEHAM PROJECT_407 |  |  | LYNEHAM | DIESEL | 11kV | CONNECTED | 2.75
MALMESBURY PROJECT_455 |  |  | MALMESBURY | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.5
SUTTON BENGER PROJECT_589 |  |  | SUTTON BENGER | BATTERY | 11kV | ACCEPTED | 0.914
BRUTON PROJECT_449 |  |  | BRUTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.202
CODFORD PROJECT_418 |  |  | CODFORD | ANAEROBIC DIGESTER | 11kV | CONNECTED | 2
CROCKERTON PROJECT_415 |  |  | CROCKERTON | STEAM TURBINE | 11kV | CONNECTED | 1
FROME PROJECT_448 |  |  | FROME | CHP - GAS TURBINE | 11kV | CONNECTED | 0.05
FROME PROJECT_594 |  |  | FROME | GAS TURBINE | 11kV | ACCEPTED | 2.67
HAWKERIDGE PROJECT_450 |  |  | HAWKERIDGE | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.08
HAWKERIDGE PROJECT_451 |  |  | HAWKERIDGE | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.1
HAWKERIDGE PROJECT_578 |  |  | HAWKERIDGE | NATURAL GAS | 11kV | ACCEPTED | 7.56
HAWKERIDGE PROJECT_593 |  |  | HAWKERIDGE | GAS TURBINE | 11kV | ACCEPTED | 7.6
HOLWELL PROJECT_436 |  |  | HOLWELL | WIND FARM | 11kV | CONNECTED | 0.5
HOLWELL PROJECT_437 |  |  | HOLWELL | WIND FARM | 11kV | CONNECTED | 0.5
WESTBURY PROJECT_404 |  |  | WESTBURY | LANDFILL GAS | 11kV | CONNECTED | 4.76
ASHTON PARK PROJECT_443 |  |  | ASHTON PARK | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
ASHTON PARK PROJECT_713 |  |  | ASHTON PARK | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.175
AVON RUBBER PROJECT_458 |  |  | AVON RUBBER | PV AND BATTERY | 11kV | ACCEPTED | 0.14
BRADFORD-ON-AVON PROJECT_597 |  |  | BRADFORD-ON-AVON | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.125
BROMHAM PROJECT_452 |  |  | BROMHAM | GAS TURBINE | 11kV | CONNECTED | 0.4
CORSHAM PROJECT_416 |  |  | CORSHAM | OTHER SYNCHRONOUS | 11kV | CONNECTED | 2
DEVIZES PROJECT_429 |  |  | DEVIZES | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.3
DEVIZES PROJECT_598 |  |  | DEVIZES | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.068
MELKSHAM TOWN PROJECT_417 |  |  | MELKSHAM TOWN | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.5
MELKSHAM TOWN PROJECT_468 |  |  | MELKSHAM TOWN | GAS TURBINE | 11kV | ACCEPTED | 7.2
SPRING QUARRY WEST PROJECT_445 |  |  | SPRING QUARRY WEST | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 7
SPRING QUARRY WEST PROJECT_467 |  |  | SPRING QUARRY WEST | GAS TURBINE | 11kV | ACCEPTED | 5
TROWBRIDGE TOWN PROJECT_444 |  |  | TROWBRIDGE TOWN | DIESEL | 11kV | CONNECTED | 2.5
WEST GRAFTON VILLAGE PROJECT_427 |  |  | WEST GRAFTON VILLAGE | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.18
CIRENCESTER TOWN PROJECT_505 |  |  | CIRENCESTER TOWN | PV & BATTERY | 11kV | ACCEPTED | 1
PARK NORTH PROJECT_519 |  |  | PARK NORTH | CHP - SPARK IGNITION | 11kV | ACCEPTED | 1
STANTON FITZWARREN PROJECT_491 |  |  | STANTON FITZWARREN | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
STANTON FITZWARREN PROJECT_492 |  |  | STANTON FITZWARREN | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3.5
STRATTON PROJECT_497 |  |  | STRATTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.71
STRATTON PROJECT_498 |  |  | STRATTON | DIESEL | 11kV | CONNECTED | 2
STRATTON PROJECT_514 |  |  | STRATTON | BATTERY | 11kV | ACCEPTED | 1.36
STRATTON PROJECT_590 |  |  | STRATTON | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.526
SWINDON PROJECT_485 |  |  | SWINDON | DIESEL | 11kV | CONNECTED | 1.781
SWINDON PROJECT_507 |  |  | SWINDON | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 2.5
SWINDON PROJECT_512 |  |  | SWINDON | BATTERY | 11kV | ACCEPTED | 1.2
SWINDON PROJECT_657 |  |  | SWINDON | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.163
TRADING ESTATE PROJECT_473 |  |  | TRADING ESTATE | DIESEL | 11kV | CONNECTED | 0.42
TRADING ESTATE PROJECT_504 |  |  | TRADING ESTATE | CHP - SPARK IGNITION | 11kV | CONNECTED | 2.15
WOOTTON BASSETT PROJECT_474 |  |  | WOOTTON BASSETT | WASTE TO ENERGY | 11kV | CONNECTED | 2
WOOTTON BASSETT PROJECT_475 |  |  | WOOTTON BASSETT | LANDFILL GAS | 11kV | CONNECTED | 2
WOOTTON BASSETT PROJECT_483 |  |  | WOOTTON BASSETT | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
WOOTTON BASSETT PROJECT_522 |  |  | WOOTTON BASSETT | LANDFILL GAS | 11kV | ACCEPTED | 6.5
WOOTTON BASSETT PROJECT_659 |  |  | WOOTTON BASSETT | GAS TURBINE | 11kV | ACCEPTED | 7.5
QUARRY ROAD PROJECT_509 |  |  | QUARRY ROAD | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 1.8
TOOTHILL PROJECT_472 |  |  | TOOTHILL | LANDFILL GAS | 11kV | CONNECTED | 2
TOOTHILL PROJECT_656 |  |  | TOOTHILL | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.058
WROUGHTON PROJECT_500 |  |  | WROUGHTON | LANDFILL GAS | 11kV | CONNECTED | 2
WROUGHTON PROJECT_501 |  |  | WROUGHTON | LANDFILL GAS | 11kV | CONNECTED | 2
WROUGHTON PROJECT_513 |  |  | WROUGHTON | CHP - GAS TURBINE | 11kV | ACCEPTED | 7
BASSETT PROJECT_719 |  |  | BASSETT | LANDFILL GAS | 11kV | ACCEPTED | 0.21
BASSETT PROJECT_728 |  |  | BASSETT | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.021
BEVOIS VALLEY PROJECT_532 |  |  | BEVOIS VALLEY | CHP - GAS TURBINE | 6.6kV | CONNECTED | 1
BEVOIS VALLEY PROJECT_722 |  |  | BEVOIS VALLEY | CHP - GAS TURBINE | 11kV | CONNECTED | 0.175
DUNBRIDGE PROJECT_591 |  |  | DUNBRIDGE | PV & BATTERY | 0.4kV | ACCEPTED | 0.044
EASTLEIGH NORTH PROJECT_528 |  |  | EASTLEIGH NORTH | LANDFILL GAS | 11kV | CONNECTED | 2.92
EASTLEIGH NORTH PROJECT_542 |  |  | EASTLEIGH NORTH | OTHER SYNCHRONOUS | 0.4kV | CONNECTED | 1
HARESTOCK PROJECT_716 |  |  | HARESTOCK | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.42
HARESTOCK PROJECT_726 |  |  | HARESTOCK | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.05
MAYBUSH PROJECT_526 |  |  | MAYBUSH | NATURAL GAS | 11kV | CONNECTED | 2
REGENTS PARK PROJECT_530 |  |  | REGENTS PARK | WASTE TO ENERGY | 11kV | CONNECTED | 1.2
SILKSTEAD PROJECT_548 |  |  | SILKSTEAD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.5
SILKSTEAD PROJECT_717 |  |  | SILKSTEAD | OTHER SYNCHRONOUS | 11kV | ACCEPTED | 0.37
SILKSTEAD PROJECT_720 |  |  | SILKSTEAD | OTHER SYNCHRONOUS | 11kV | ACCEPTED | 0.2
ST CROSS PROJECT_724 |  |  | ST CROSS | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.064
TOTTON PROJECT_549 |  |  | TOTTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2
VELMORE PROJECT_529 |  |  | VELMORE | DIESEL | 11kV | CONNECTED | 1.5
WESTERN ESPLANADE PROJECT_682 |  |  | WESTERN ESPLANADE | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.18
WESTERN ESPLANADE PROJECT_721 |  |  | WESTERN ESPLANADE | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.18
GREENFORD PROJECT_556 |  |  | GREENFORD | NATURAL GAS | 11kV | CONNECTED | 1

## Quoted Jobs
Project Name | GSP Parent | BSP Parent | PS Parent | Technology Type | Capacity (MVA) | Quotation Expiry Date | Contestable Costs | Non-Contestable Costs | Reinforcement Works
BOTLEYWOOD_PROJECT_1 | BOTLEY WOOD GSP |  |  | Natural Gas | 1.26 | 44474 | N/A | 300 | N/A
BOTLEYWOOD_PROJECT_2 | BOTLEY WOOD GSP |  |  | Photovoltaic Plant | 499.2 | 44543 | 5994585.28 | 1173806 | N/A
BRAMLEYAT_PROJECT_1 | BRAMLEY (ANDO-THAT) |  |  | PV & Battery | 18 | 44492 | 4851542.89 | 3816373.39 | 4785413.6
BRAMLEYAT_PROJECT_2 | BRAMLEY (ANDO-THAT) |  |  | PV & Battery | 14 | 44494 | 6546986.79 | 3856549.54 | 199356
BRAMLEYBASI_PROJECT_1 | BRAMLEY (BASI) |  |  | Photovoltaic Plant | 35 | 44490 | N/A | 1805281.6 | N/A
BRAMLEYBASI_PROJECT_2 | BRAMLEY (BASI) |  |  | Battery | 5 | 44537 | 283519.03 | 223469.51 | N/A
CHICKERELL_PROJECT_1 | CHICKERELL GSP |  |  | Photovoltaic Plant | 6 | 44545 | 106049.42 | 90550.62 | N/A
COWLEY_PROJECT_1 | COWLEY |  |  | Photovoltaic Plant | 12.5 | 44496 | 378914.59 | 378425.79 | 9731.09
COWLEY_PROJECT_2 | COWLEY |  |  | Battery | 49.9 | 44500 | N/A | 1115719.55 | 661175.66
COWLEY_PROJECT_3 | COWLEY |  |  | PV & Gas | 99.8 | 44537 | 7959320.02 | 1303472.6 | N/A
COWLEY_PROJECT_4 | COWLEY |  |  | PV & Battery | 35 | 44538 | 4895532.08 | 1320300.4 | N/A
FAWLEY_PROJECT_1 | FAWLEY |  |  | Tidal | 14.877 | 44488 | 2813237.04 | 494127.84 | 42034.77
FAWLEY_PROJECT_2 | FAWLEY |  |  | Tidal | 19.836 | 44488 | 3868131.36 | 1549022.16 | 1091757.63
FAWLEY_PROJECT_3 | FAWLEY |  |  | Tidal | 29.754 | 44488 | 11711959.74 | 624891.34 | 70077.91
FAWLEY_PROJECT_4 | FAWLEY |  |  | PV & Battery | 36 | 44535 | N/A | 681763.57 | 122308.66
FLEETBRAMLEY_PROJECT_1 | FLEET BRAMLEY |  |  | Natural Gas | 20 | 44476 | 1060220.38 | 180624.62 | N/A
FLEETBRAMLEY_PROJECT_2 | FLEET BRAMLEY |  |  | Photovoltaic Plant | 49.9 | 44479 | 9037747.36 | 1397671.6 | N/A
FLEETBRAMLEY_PROJECT_3 | FLEET BRAMLEY |  |  | Battery | 150 | 44489 | 25132480.15 | 19852861.4 | N/A
FLEETBRAMLEY_PROJECT_4 | FLEET BRAMLEY |  |  | Landfill Gas | 7 | 44549 | 494807.89 | 3328243.26 | 5547.29
LALEHAM_PROJECT_1 | LALEHAM |  |  | PV & Battery | 81 | 44483 | N/A | 1978256.6 | N/A
MANNINGTON_PROJECT_1 | MANNINGTON GSP |  |  | Battery | 8.55 | 44503 | 1430801.5 | 388367.81 | N/A
MANNINGTON_PROJECT_2 | MANNINGTON GSP |  |  | Battery | 94.962 | 44510 | 4346829.95 | 2728673.47 | 227166.87
MANNINGTON_PROJECT_3 | MANNINGTON GSP |  |  | Photovoltaic Plant | 49.875 | 44535 | 11784656.53 | 2393697.09 | 31307.47
MANNINGTON_PROJECT_4 | MANNINGTON GSP |  |  | Photovoltaic Plant | 28 | 44539 | 6601297.86 | 3556836.25 | N/A
MELKSHAM_PROJECT_1 | MELKSHAM |  |  | Photovoltaic Plant | 26 | 44508 | 8685714.98 | 1373518.77 | N/A
MELKSHAM_PROJECT_2 | MELKSHAM |  |  | Photovoltaic Plant | 30 | 44531 | 3113353.81 | 1336546.37 | N/A
MINETY_PROJECT_1 | MINETY |  |  | PV & Battery | 49.9 | 44539 | 15779738.46 | 1265672.67 | 26963.34
NURSLING_PROJECT_1 | NURSLING |  |  | Photovoltaic Plant | 12 | 44501 | 774318.27 | 1718873.2 | N/A
NURSLING_PROJECT_2 | NURSLING |  |  | Battery | 49 | 44509 | N/A | 916258.6 | N/A